## Planilha1
pag | type | equipament | problem | cause | action
1 | mechanical | pumps | pump too hot and flashing off; pump churningup fluid and failing to discharge water after na initial surge and then continue to recirculate | unloading valve not working properly | repair or replace the unloading valve
1 | mechanical | pumps | pump too hot and flashing off; pump churningup fluid and failing to discharge water after na initial surge and then continue to recirculate | excessive wear in pump | repair or repplace the pump
1 | mechanical | pumps | pump too hot and flashing off; pump churningup fluid and failing to discharge water after na initial surge and then continue to recirculate | relif valve set too high | adjust the relief valve
1 | mechanical | pumps | pump too hot and flashing off; pump churningup fluid and failing to discharge water after na initial surge and then continue to recirculate | discharge valve throttled or closed | open the discharge valve
1 | mechanical | pumps | pump too hot and flashing off; pump churningup fluid and failing to discharge water after na initial surge and then continue to recirculate | leak in suction piipe; packing or seal worm | inspect the line for broken or loose connections to determine the source of the leak
2 | mechanical | pumps | pump churning up fluid and failing to discharge water after na initial surge and then continuing to recirculate (continued) | lift too great; discharge line blocked chocked up filter | report this as na engineering problem; it may require design changes; clean filters
2 | mechanical | pumps | pump churning up fluid and failing to discharge water after na initial surge and then continuing to recirculate (continued) | suction pipe too long | report this as na engineering problem; it may require design changes
2 | mechanical | pumps | pump churning up fluid and failing to discharge water after na initial surge and then continuing to recirculate (continued) | insufficient head; suction valve shut | increase the supply source level
2 | mechanical | pumps | pump churning up fluid and failing to discharge water after na initial surge and then continuing to recirculate (continued) | too much air in the system | check the suction system and glands for airs ingress; if the source is from a pound, check to see if there are any whirlpools sucking air into the system; throttle the pump to reduce the rate of withdraw from the supply source
3 | mechanical | pumps | heavy vibrations during the operation of the pump | pump and motor out of alignment; bem shaft; cavitation; recirculation; unusual wear | perform vibration analysis to determine the source of the problem(s); mechanical maintenance should conduct alignment checks and make the necessary adjustments
3 | mechanical | pumps | heavy vibrations during the operation of the pump | some rotating element broken off, causing na unbalanced condition | perform vibration analysis to determine the source of the problem; mechanical maintenance should conduct balancing corrections
4 | mechanical | pumps | heavy vibrations during the operation of the pump (continued) | cavitation from lack of net positive suction head or turbulence from sharp pipe bends immediately upstream of the pump; suction pressure lower than the corresponding saturation temperature | Lower the suction temperature.
4 | mechanical | pumps | heavy vibrations during the operation of the pump (continued) | Recirculation due to blocked or narrowed discharge line | Increase the clearance at the exit tips of vanes to eliminate and avoid discharge restrictions.
4 | mechanical | pumps | heavy vibrations during the operation of the pump (continued) | Obstruction lodged in one side of the impeller | Have maintenance open the pump casing and remove any obstruction that may be there; Check to ensure that there is no further damage.
5 | mechanical | pumps | Heavy vibrations during the operation of the pump (continued) | Lack of lubricant or over-lubrication | Inspect the oil well sight glasses, or check the dipsticks; Add lubricant as necessary; Detennine if the proper grade of lubricant is being used; Change the lubricant if necessary
5 | mechanical | pumps | Heavy vibrations during the operation of the pump (continued) | Pump not tumed regularly when sitting idle | The pump should be turned frequently when it is on standby to avoid false brinelling and other surface defects on bearings
5 | mechanical | pumps | Heavy vibrations during the operation of the pump (continued) | Incorrect installation | Contact mechanical maintenance to have the installation checked
6 | mechanical | pumps | Capacity or pressure of the pump reduced; Pump failing to deliver water | Wrong direction of rotation | Check the direction of the arrow that is usually cast on the casing to verify the rotation direction; Have electricians check the wiring connections and correct them
6 | mechanical | pumps | Capacity or pressure of the pump reduced; Pump failing to deliver water | Discharge line blocked | Check the direction of the arrow that is usually cast on the casing to verify the rotation direction; Have electricians check the wiring connections and correct them
6 | mechanical | pumps | Capacity or pressure of the pump reduced; Pump failing to deliver water | Discharge valve closed | Check the direction of the arrow that is usually cast on the casing to verify the rotation direction; Have electricians check the wiring connections and correct them
6 | mechanical | pumps | Capacity or pressure of the pump reduced; Pump failing to deliver water | Impeller mounted incorrectly | Have mechanical maintenance verify the impeller mounting and reverse the impeller on the shaft.
6 | mechanical | pumps | Capacity or pressure of the pump reduced; Pump failing to deliver water | Mechanical defects, such as worn rings, damaged impeller, or a defective casing gasket | Have maintenance verify and correct the problem
6 | mechanical | pumps | Capacity or pressure of the pump reduced; Pump failing to deliver water | Clogged filters | Check the pressure differential across the filter; If the differential is too high, change and clean filters
7 | mechanical | pumps | Motor using excessive power at rated temperature; Motor protection relay being tripped by pump | Required differential head or pressure lower than rated | Throttle the dischargevalve until the rated capacity is reached
8 | mechanical | pumps | Bearings running hot | Improper alignment | Perform Phase Angle analysis to determine piping misalignment; Perform soft-foot analysis; Cheek to see if correct grease is used and correct application; Determine if bearing was installed per manufacturer's procedure
8 | mechanical | pumps | Bearings running hot | Piping misalignment | Perform Phase Angle analysis to determine piping misalignment; Perform soft-foot analysis; Cheek to see if correct grease is used and correct application; Determine if bearing was installed per manufacturer's procedure
8 | mechanical | pumps | Bearings running hot | Bent shaft | Perform Phase Angle analysis to determine piping misalignment; Perform soft-foot analysis; Cheek to see if correct grease is used and correct application; Determine if bearing was installed per manufacturer's procedure
8 | mechanical | pumps | Bearings running hot | Poor lubrication | Perform Phase Angle analysis to determine piping misalignment; Perform soft-foot analysis; Cheek to see if correct grease is used and correct application; Determine if bearing was installed per manufacturer's procedure
8 | mechanical | pumps | Bearings running hot | Overgreasing | Perform Phase Angle analysis to determine piping misalignment; Perform soft-foot analysis; Cheek to see if correct grease is used and correct application; Determine if bearing was installed per manufacturer's procedure
8 | mechanical | pumps | Bearings running hot | Poor foundations | Perform Phase Angle analysis to determine piping misalignment; Perform soft-foot analysis; Cheek to see if correct grease is used and correct application; Determine if bearing was installed per manufacturer's procedure
8 | mechanical | pumps | Bearings running hot | Improperly fitted bearings | Perform Phase Angle analysis to determine piping misalignment; Perform soft-foot analysis; Cheek to see if correct grease is used and correct application; Determine if bearing was installed per manufacturer's procedure
9 | mechanical | pumps | Bearings waning hot (continued) | Bearing substitute used and never replaced with original specification model | Use the maintenance management tracking system to see if the bearing was replaced in an emergency with a substitute bearing because it was "close enough," and the substitute was never replaced with the correct one.
9 | mechanical | pumps | Insufficient discharge | Air leaks in suction line or stuffing box | Tighten the glands slightly; Check the suction line for leaks
9 | mechanical | pumps | Insufficient discharge | Wear rings worn or damaged | Replace wear rings; Determine correct wear ring clearances
9 | mechanical | pumps | Insufficient discharge | Foot valve too small | Determine the proper size of the foot valve.
10 | mechanical | pumps | Excessive power consumption; bent shaft | Speed too high | Determme the correct speed and specrfic gravrty or viscosity; A design change may be required
10 | mechanical | pumps | Excessive power consumption; bent shaft | Specific gravity or viscosity too high | Determme the correct speed and specrfic gravrty or viscosity; A design change may be required
10 | mechanical | pumps | Excessive power consumption; bent shaft | Bent shaft | Replace the shaft
10 | mechanical | pumps | Excessive power consumption; bent shaft | Rotating element binds | Remove the shaft and inspect
10 | mechanical | pumps | Excessive power consumption; bent shaft | Stuffing boxes too tight | Loosen the gland slightly if the stuffing box is too tight
10 | mechanical | pumps | Excessive power consumption; bent shaft | Wearing rings worn | Replace the rings
11 | mechanical | bearings | overhating | Wrong type of grease or oil causing breakdown of the lubricant | Consult with the lubricant manufacturer to verify correct grade of lubricant, and replace the old grease or oil with the correct one.
11 | mechanical | bearings | overhating | Low oil level | Add oil until the oil level is just below the center of the lowest ball or roller in the bearing
11 | mechanical | bearings | overhating | loss of oil through the seal | Add oil until the oil level is just below the center of the lowest ball or roller in the bearing
11 | mechanical | bearings | overhating | Housing overpacked with grease, causing excessive churning of the lubricant | Purge the bearing until only the lower half is 1/2 to 2/3 full of grease
11 | mechanical | bearings | overhating | Inadequate internal clearance from using substitute bearing | Replace with a bearing that meets the original design specification
12 | mechanical | bearings | overhating (continued) | Housing bore out of round | Determine what the true bore is and scrape the housing to relieve the pinching of the bearing
12 | mechanical | bearings | overhating (continued) | housing warped | Determine what the true bore is and scrape the housing to relieve the pinching of the bearing
12 | mechanical | bearings | overhating (continued) | Rotating seals rubbing against stationary parts | Check the running clearance of the rotating seal to eliminate the rubbing; Check the alignment of the bearing
12 | mechanical | bearings | overhating (continued) | Blocked oil return holes | Clean the holes. Investigate type of debris
12 | mechanical | bearings | overhating (continued) | Unbalanced load | Rebalance the machine; Replace the housing with one having the correct size bore
12 | mechanical | bearings | overhating (continued) | housing bore too large | Rebalance the machine; Replace the housing with one having the correct size bore
13 | mechanical | bearings | overhating (continued) | Incorrect oil level causing insufficient oil to reach the bearing | Clean the clogged holes to vent the oil gauge; Ensure bearing material is not the clogging agent; If it is, the bearing may have to be overhauled or replaced
13 | mechanical | bearings | overhating (continued) | Wrong type of lubricant, which has broken down and lost its lubricating properties | Check oil specs for the machine, and use the correct grade of lubricant.
14 | mechanical | bearings | Noisy bearing; Irregular Dents or Material Embedded in Raceways | Foreign matter such as dirt, sand, and carbon entering the bearing housing | Clean out the bearing housing. Replace any worn seals
14 | mechanical | bearings | Noisy bearing; Irregular Dents or Material Embedded in Raceways | Brinnelling | Rotate shafts 1/: turn in all stationary machines at least once per two weeks.
14 | mechanical | bearings | Noisy bearing; Irregular Dents or Material Embedded in Raceways | Static electrical arcing in the bearings | Ensure insulation and grounding gear is in good order.
15 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | Corrosive agents entering the bearing | Add a shroud or a finger to throw off any foreign matter.
15 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | Failure to remove foreign matter from the bearing housing before assembling the bearing unit | Carefully clean the housing, and always use fresh lubricant.
15 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | A flat on a ball or a roller due to skidding | Replace the bearing
16 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | Incorrectly mounted bearing | Replace the bearing without hammering any part of it; Use a press to install bearing or unifomily heat or chill bearing to set it
16 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | bearing hammered onto the shalt or into the housing | Replace the bearing without hammering any part of it; Use a press to install bearing or unifomily heat or chill bearing to set it
16 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | Interference of other movable parts of the machine | Check every moving part for interference; Reset the parts to provide the necessary clearance.
16 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | Unbalanced load | Rebalance the unit; Replace the housing with one that has the correct size bore.
16 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | housing bore too large | Rebalance the unit; Replace the housing with one that has the correct size bore.
16 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | Bearing exposed to resonance-caused vibration while the machine is idle | Carefully examine the bearing for wear spots that are separated by the distance equal to the spacing of the balls; Replace the bearings
17 | mechanical | bearings | Vibration | Distortion of shaft and inner ring | Re-machine the shaft fillet to obtain the correct support.
17 | mechanical | bearings | Vibration | Distortion of the housing and outer ring, causing pinching of the bearing | Remachine the housig fillet to obtain the correct support; Check manufacturer's tolerance measurement guides.
17 | mechanical | bearings | Vibration | Rotating seals rubbing against the stationary parts | Check the running clearance of the rotating seals to eliminate rubbing
17 | mechanical | bearings | Vibration | Incorrectly mounted bearing as indicated by hammer blow signs on the bearing | Replace with a new bearing without hammering it into place; Follow the bearing manufacturer's fitting recommendations.
17 | mechanical | bearings | Vibration (continued) | Inadequate support in the housing, causing the outer ring to cock | Remachine the housing fillet to relieve stress; Re-machining may require a shoulder collar.
18 | mechanical | bearings | Vibration (continued) | General vibration of the machine | Check the balance of the machine; Rebalance the machine if necessary
18 | mechanical | bearings | Vibration (continued) | Shaft and housing shoulders and face of the locking nut not square with the bearing seat | Remachine the parts to obtain squareness; Ensure that there is a radius machined in at root of shoulder to minimize stress riser
19 | mechanical | bearings | Bearing loose on the shaft | Shaft diameter too small or adapter not tight enough | Metalhze the shaft, and regrmd it to obtain a proper fit; Retighten the adapter to get a firmer grip on the shaft
19 | mechanical | bearings | Bearing loose on the shaft | Knurling and center punching of the bearing seat on the shaft, causing the high spots to be flattened when the load is applied | Metallize and regrind the shafi to the proper size; Stress relieve shaft before putting it back into service
19 | mechanical | bearings | Bearing loose on the shaft | loose fitting shaft | Metallize and regrind the shafi to the proper size; Stress relieve shaft before putting it back into service
20 | mechanical | bearings | Shaft difficult to turn by hand | Inadequate shoulder support in the housing causing bending of the shaft | Remachine the shaft fillet to relieve the stress; This may require a shoulder collar to be fitted.
20 | mechanical | bearings | Shaft difficult to turn by hand | Distortion of the bearing seals | Remachine the housing shoulder to clear the seal.
20 | mechanical | bearings | Shaft difficult to turn by hand | Bearing seat diameter machined oversize, causing excessive expansion of the shaft and bearing inner ring, thus reducing the clearance in the bearing | Grind and hone the shaft to obtain a proper fit between the inner ring of the bearing and the shaft.
21 | mechanical | bearings | Shaft difficult to turn by hand | Incorrect linear or angular alignment of two or more coupled shafts with two or more bearings | Shim the pillow blocks to correct the alignment; Ensure that the shafts are coupled in a straight line;This is especially important when three or more bearings operate on one shaft
21 | mechanical | bearings | Shaft difficult to turn by hand | Distortion of the housing and the outer ring causing pinching of the bearing | Remachme the housing fillet to obtain the proper support.
21 | mechanical | bearings | ANGULAR MISALIGNMENT | Incorrect linear or angular alignment of two or more coupled shafts with two or more bearings | Shim the pillow blocks to correct the alignment; Ensure that the shafts are coupled in a straight line;This is especially important when three or more bearings operate on one shaft
21 | mechanical | bearings | ANGULAR MISALIGNMENT | Distortion of the housing and the outer ring causing pinching of the bearing | Remachme the housing fillet to obtain the proper support.
21 | mechanical | bearings | Frequent replacements | Unequal load distribution on the bearing | Rework the shaft, the housing, or both to obtain a proper fit; A new shaft may be required
22 | mechanical | bearings | Oil leakage | Air flowing over the bearings, for example, a forced draft fan with air inlet over the bearings | Provide adequate baffling to divert the direction of the airflow.
22 | mechanical | bearings | Oil leakage | Oil leakage at the housing split causing excessive loss of lubricant | Use a thin layer of gasket cement to seal off the leakage; Shut down the equipment if the leakage is excessive
22 | mechanical | bearings | Oil leakage | Failure to remove debris from the bearing housing before assembling the bearing unit | Always carefully clean the housing, and use fresh lubricant
23 | mechanical | valves | Valve gland leakage | Packing too loose | Tighten the packing enough to stop the leak.
23 | mechanical | valves | Valve gland leakage | Packing reached the end of its useful life | Repack the gland with new correct sized packing rings.
23 | mechanical | valves | Valve gland leakage | Insufficient number of turns of packing | Check the number of packing rings that should be in the gland. Repack the gland with sufficient turns.
23 | mechanical | valves | Valve gland leakage | Packing ring butts all in line | Stagger the ring butts by placing the first at O°the next at 180° and then a 90°-270°; Repeat the rotating sequence until the stuffing box is filled
23 | mechanical | valves | Valve gland leakage | Valve stem badly scored | Replace valve stem; Check why it is scored first
24 | mechanical | valves | Valve gland leakage (continued) | Wrong grade packing material | Replace with the correct grade.
24 | mechanical | valves | Valve gland leakage (continued) | Cocked gland follower | Adjust the gland follower to correctly place the follower at a 90° angle to the stem axis.
25 | mechanical | valves | Body to bonnet gasket leakage | Gasket beyond the 60% crush factor | Replace the gasket with a new one; Smear the gasket surfaces with a suitable lubricant to help preserve it.
25 | mechanical | valves | Body to bonnet gasket leakage | Wrong type of gasket material | Replace the gasket with a new one; Smear the gasket surfaces with a suitable lubricant to help preserve it.
25 | mechanical | valves | Body to bonnet gasket leakage | Hammer-cut gasket and fibers destroyed | Replace the gasket; Gaskets should always be cut with a circular cutter and holes put in using a belt punch.
26 | mechanical | valves | Body to bonnet gasket leakage (continued) | Wrong gasket material | Replace with the correct gasket material; The most expensive material is not always the best; Use the gasket material that is recommended for the application.
26 | mechanical | valves | Body to bonnet gasket leakage (continued) | Gasket landing surfaces dirty | Replace with the correct gasket material; The most expensive material is not always the best; Use the gasket material that is recommended for the application.
26 | mechanical | valves | Body to bonnet gasket leakage (continued) | Gasket landing grooved by wire-drawing | Replace with the correct gasket material; The most expensive material is not always the best; Use the gasket material that is recommended for the application.
26 | mechanical | valves | Body to bonnet gasket leakage (continued) | Scored body or bonnet seal faces | Machine finish the gasket landing faces, and maintains them in that condition; Scrape off any old gasket debris, and ensure that the surfaces are left clean.
26 | mechanical | valves | Body to bonnet gasket leakage (continued) | Body/or bonnet bolts improperly tightened | Torque the bolts down in a star pattern to ensure that the joint is squarely made.
27 | mechanical | valves | Body to bonnet gasket leakage (continued) | Gasket too old and pressure blown | Replace with a new gasket; New gaskets should always be used for replacements; Never reuse the old gasket.
28 | mechanical | valves | Gate valve difficult to operate | Packing gland too tight | Adjust the packing until the valve operates easily.
28 | mechanical | valves | Gate valve difficult to operate | Too many turns of packing installed | Check the drawing for the correct number of turns required, and adjust.
28 | mechanical | valves | Gate valve difficult to operate | Piping misalignment | Break the joint, and correctly realign the pipe to the valve; Align piping with zero cold spring .
28 | mechanical | valves | Gate valve difficult to operate | Bent valve stem | Straighten the stem to +/- 0.002" TIR max
28 | mechanical | valves | Gate valve difficult to operate | Wrong size handwheel or motor operator | Check the specifications, and replace with the proper handwheel.
29 | mechanical | valves | Gate valve hard to operate (continued) | Stern threads or nut damaged | Clean the threads, using thread chaser.
29 | mechanical | valves | Gate valve hard to operate (continued) | Thermal binding of valve closed | Contact maintenance; To prevent this problem from occurring, avoid forcing the valve into the seat in high temperature systems.
30 | mechanical | valves | Gate valve hard to operate (continued) | Piping misaligned | Avoid twisting valve body, especially check valves, gate valves and butterfly valves.
30 | mechanical | valves | Gate valve hard to operate (continued) | Valve internals out of alignment due to body stresses caused when piping 10 valve is misaligned | Avoid twisting valve body, especially check valves, gate valves and butterfly valves.
31 | mechanical | valves | Gate valve chattering | Valve being used to throttle flow | Adjust the valve to fully open or fully closed; Gate valves are not designed to control or throttle flow; Do not use them for this function.
31 | mechanical | valves | Gate valve chattering | Piping distortion due to loading or temperature distortion | Install spring hangers, and check the valve to the piping nozzle alignment; Piping to valve alignment should have zero-cold-spring; In other words, both connections should be perfectly aligned with each other with no stress.
32 | mechanical | valves | Gate valve chattering (continued) | Partially open valve | Open or shut the valve completely; The gate valve should always be fully open or shut.
32 | mechanical | valves | Gate valve chattering (continued) | Natural vibration frequency being excited by some other natural or induced vibration frequency | Change the mass by stiffening the valve; Add a weight to the pipe as close as possible to the valve.
32 | mechanical | valves | Gate valve chattering (continued) | Rising stem valve in confined space restricting full opening | Change the valve for a non-rising stem valve.
32 | mechanical | valves | Gate valve chattering (continued) | Stem lock nut on yoke loose | Tighten the yoke nut.
33 | mechanical | valves | Leakage across the disc and seat in a globe valve | Erosion across the seat face | \Caution\During throttling Operations, do not close the valve far enough to induce a high-pitched screaming noise.
33 | mechanical | valves | Leakage across the disc and seat in a globe valve | Reface the disc and seat, and lap to ensure good contact all around the faces. | \Caution\During throttling Operations, do not close the valve far enough to induce a high-pitched screaming noise.
33 | mechanical | valves | Leakage across the disc and seat in a globe valve | Seat contact surface area too wide | Machine the disc and seat to produce a very narrow contact band around the seat and disc faces; Ideally, maintain a 05° differential angle between the seat and disc faces.
33 | mechanical | valves | Leakage across the disc and seat in a globe valve | Incorrect valve in the system | Change the valve immediately if the valve israted at 200 WOG and 125 S and is operating in a 400-psi steam system.
34 | mechanical | valves | Leakage across the disc and seat in a globe valve (continued) | Incorrect valve in the system (continued) | \Warning\ If the valve is overpressurized, it is dangerous to operate at this pressure; It should be operating at no more than 200 psi in a water, oil, or gas system, and no more than 125 psi in steam system.
35 | mechanical | valves | Intermittent leakage across the valve | Disc cocking due to bent valve stem | Remove the stem, and check the TIR. Straighten the valve stem.
35 | mechanical | valves | Intermittent leakage across the valve | Disc sticking due to slightly ofi center misalignment of bonnet stem threads | Change the valve; Check piping alignment to the valve body; Piping should have zero cold spring with valve nozzle.
35 | mechanical | valves | Intermittent leakage across the valve | Stem attached to the disc nut is too tight, restricting the disc from self-centering in the seat | Add shims one at a time between the stem nut and disc shoulder until sufficient float is achieved.
36 | mechanical | valves | Screwed bonnet loosening off repeatedly | Valve back-seated too tightly | Retighten the bonnet lock nut; \Warning\ If this problem is not corrected, the valve may blow out and cause injury; To avoid this problem, do not force the stem to the backseat against the cover, particularly using a valve wrench.
37 | mechanical | valves | Screwed bonnet loosening off repeatedly (continued) | Missing lock screw or tab | Verify the need for a lock screw or tab by reading the drawing or manufacturer's documentation, and reinstall the tab or lock screw if necessary; \Warning\ Never install a screwed bonnet globe valve in a high-pressure system or a dangerous substance system because the bonnet can become unscrewed if it is forced against the backseat.
37 | mechanical | valves | Screwed bonnet loosening off repeatedly (continued) | Bonnet lock nut not torqued to specified setpoints | Verify the setting, using a torque wrench to correct the setting if required.
38 | mechanical | valves | Piping flange leaking | Bolts improperly tightened | Loosen the bolts, and retighten properly; Flange bolts need to be tightened sequentially around the bolt pitch circle; After the first nut is tightened snugly, go 180° across to the second nut, and tighten it snugly; Go 90° to the third nut, and tighten it snugly; Go 180° to tighten the fourth nut Repeat this sequence until all the bolts are snugly tightened; Torque all nuts to specification in the same sequence to complete the tightening process.
39 | mechanical | valves | Valve to piping flange leaking (continued) | Reusing old gasket, causing old gasket material to stick to the flange surface | Scrape the flange clean of all foreign material; Ensure that the flange faces are properly aligned to each other and at the zero coldvspring setpoint; Always use a new gasket when installing a valve or making repairs.
40 | mechanical | valves | Valve to piping flange leaking (continued) | Wrongly set Flexitallie gasket | If the compression is less than 60% and no other damage is apparent, then tighten the gasket to the correct setpoint. If the compression is greater than 60%, scrap the gasket, and replace it with a new gasket; flexitallic gasket corrugations must be compressed to a minimum of 60% of the original thickness for effective sealing. If the gasket is compressed beyond 90%, it becomes ineffective.
41 | mechanical | valves | Pressure safety valve leaking | Improper setting | Correct the setting, or contact maintenance; /Warning/ Ensure that a gag is not left in place or being used to try to stop leakage across valve seat; Pressure tests the valve to lift at 110 % of the working pressure of the boiler.
41 | mechanical | valves | Pressure safety valve leaking | Valve-disc-to-seat contact area too large, causing valve simmering to take place | Reface the seat face and disc face to maintain a 1/2 degree angle differential between the points of contact.
42 | mechanical | valves | Pressure safety valve leaking (continued) | Cracked or broken compression spring | Perform a visual inspection of the spring for cracks or breaks; If the spring can be taken off valve without being broken, hang it on a string, and strike it very lightly with a peen hammer; If the spring rings loudly and clearly, it does not have a crack; If the spring makes a clunking sound, it is cracked; Replace it.
42 | mechanical | valves | Pressure safety valve leaking (continued) | Bent valve stem | Check the stem TIR to ensure that the stem is not bent. Straighten the stem if necessary.
43 | mechanical | valves | intermittent vibration on valves and associated piping | Improper loading of pipe hangers | Evaluate the current setpoints to ensure that they meet specifications.
43 | mechanical | valves | intermittent vibration on valves and associated piping | Resonance | Remove anything that should not be on the piping; Piping and valves may be loaded down with scaffolding or maintenance walkways; This can alter the mass, affecting the natural frequency and causing the scaffolding or walkways to vibrate in tune with a pump or motor having the same natural frequency; This vibration can have devastating results.
43 | mechanical | valves | intermittent vibration on valves and associated piping | Water hammer | Ensure that the steam traps are operating and do not need maintenance; Clean the traps as necessary; Open the drain valves during any plant shutdown.
44 | mechanical | valves | Continual leakage across a butterfly valve | Valve may be installed in the wrong direction | Check the direction arrow casting on the side of valve body; Reverse the body installation if the directional arrow indicates that the valve is incorrectly installed.
44 | mechanical | valves | Continual leakage across a butterfly valve | Piping misalignment with valve | Inspect and report the findings to maintenance; Piping misalignment can distort the valve body and can cause the disc shaft trunnions to get out of alignment and bind up.
44 | mechanical | valves | Continual leakage across a butterfly valve | Neoprene valve seat and gasket | Check the valve seat to ensure that it did not kink or roll during installation; Straighten as necessary.
45 | mechanical | valves | hand-operated valve difficult to open | Thread damage | Take the stem out of the valve. and run a die-nut down the thread if it is a standard thread; If it is an Acme thread, use a thread chaser or a fine file to remove any imperfections.
45 | mechanical | valves | hand-operated valve difficult to open | Shaft bent | Remove the shaft, and check TIR; Straighten the shaft, and reinstall in the valve.
45 | mechanical | valves | hand-operated valve difficult to open | Valve body twisted | Separate the pipe from the valve, and observe how far the pipe moves out of alignment; if the pipe is out of alignment, the pipe must be bent until it meets the valve nozzle with zero cold spring; /Warning/ If a hand-operated valve cannot be moved without difficulty, it requires maintenance; Never force a valve by using a wrench.
45 | mechanical | valves | hand-operated valve difficult to open | piping misaligned to valve body | Separate the pipe from the valve, and observe how far the pipe moves out of alignment; if the pipe is out of alignment, the pipe must be bent until it meets the valve nozzle with zero cold spring; /Warning/ If a hand-operated valve cannot be moved without difficulty, it requires maintenance; Never force a valve by using a wrench.
46 | mechanical | valves | Hand-operated valve difficult to open | Bonnet stem nut out of alignment with valve seat | Contact maintenance and the machineshop to correct this problem and replace the valve.
46 | mechanical | valves | Hand-operated valve difficult to open | Gland packing too tight | Slacken off the gland follower, and allow the packing to move slightly.
46 | mechanical | valves | Hand-operated valve difficult to open | Gland packing badly installed | Repack the valve.
47 | mechanical | chain drives | Noisy drive | Incorrect tension | Check the slack side span for 2% deflection, and adjust the chain tension as necessary.
47 | mechanical | chain drives | Noisy drive | Insufficient lubrication | Check the drive for proper lubrication; Lubricate the drive as necessary.
47 | mechanical | chain drives | Noisy drive | Worn drive | Check the chain and sprocket for wear, and have it replaced if worn.
47 | mechanical | chain drives | Noisy drive | Misalignment of sprockets | Check the alignment, and realign as necessary.
47 | mechanical | chain drives | Noisy drive | Loose casing or bearings | Draw up all bolts, and brace the casings as required.
47 | mechanical | chain drives | Noisy drive | Pitch too large | Check chain drive spec chart; Change the chain.
48 | mechanical | chain drives | Chain climbing sprocket teeth | Chain worn | Check for chain wear. Replace chain as necessary.
48 | mechanical | chain drives | Chain climbing sprocket teeth | Insufficient tension | Check chain tension. Increase tension as needed.
48 | mechanical | chain drives | Chain climbing sprocket teeth | Material in tooth pockets | Clean sprocket. Eliminate cause of material buildup.
48 | mechanical | chain drives | Chain climbing sprocket teeth | Chains & sprockets fit poorly | Notify the maintenance department.
48 | mechanical | chain drives | Chain climbing sprocket teeth | Insufficient chain wrap | Change the driver arrangement to get more sprocket-teeth in contact with the chain, or use an idler take-up sprocket to increase the wrap.
48 | mechanical | chain drives | Chain climbing sprocket teeth | Excessive chain slack | Adjust the centers or take-up sprockets for a 2% final deflection.
49 | mechanical | chain drives | Drive is running excessrvely hot | Running too fast | Check drive for proper speed. Adjust as required.
49 | mechanical | chain drives | Drive is running excessrvely hot | Insufficient lubrication | Check for the correct type and amount of lubricant.
49 | mechanical | chain drives | Drive is running excessrvely hot | Chain operating too fast for bath lubrication | Use the oil stream system to lubricate the chain.
49 | mechanical | chain drives | Drive is running excessrvely hot | Chain immersed too deeply in oil bath in bath-lubricated drive | Check the drive for obstructions, and check the guard design; Remove all obstructions.
50 | mechanical | chain drives | Chain hanging in sprocket | Wont sprocket teeth | Check for chain wear, and replace the chain as necessary.
50 | mechanical | chain drives | Chain hanging in sprocket | Material buildup on driver sprocket tooth pockets | Clean and lubricate the sprockets correctly.
50 | mechanical | chain drives | Chain hanging in sprocket | Sticky lubricant | Check the grade of the lubricant, and refer to the lubricant chart for that particular chain drive configuration; Replace with the recommended lubricant as necessary.
51 | mechanical | chain drives | Chain whip | Insufficient tension | Correct the tension; The tension should be set to deflect 2% of the pitch between the driver and the driven sprockets.
51 | mechanical | chain drives | Chain whip | Stiff chain joints | Replace the bad joints, or install a new chain.
51 | mechanical | chain drives | Chain whip | Excessive chain slack | Install a chain take-up or idler sprocket, or adjust the centers of the sprockets.
51 | mechanical | chain drives | Chain whip | High pulsating loads | Reduce the load where possible, or replace the chain with one of suitable length.
51 | mechanical | chain drives | Chain whip | Nonuniforrn chain wear | Investigate why the chain is wearing in an irregular manner; Replace the chain.
52 | mechanical | chain drives | Stiff chain joints | Misalignment of drive | Have maintenance check the alignment and correct as necessary.
52 | mechanical | chain drives | Stiff chain joints | Worn and corroded chain | Replace the chain; Provide the correct lubrication
52 | mechanical | chain drives | Stiff chain joints | Inadequate lubrication | Clean and lubricate the chain correctly; Refer to the lube manual for correct lubricant and application.
52 | mechanical | chain drives | Stiff chain joints | Corrosion on the chain | Remove any corrosion, lubricate the chain correctly, and protect the chain from further corrosion by keeping it clean and well lubricated.
52 | mechanical | chain drives | Stiff chain joints | Excessive overload | Identify the overload cause, and reduce it.
52 | mechanical | chain drives | Stiff chain joints | Material buildup in joints | Clean and lubricate the chain more frequently.
52 | mechanical | chain drives | Stiff chain joints | Peening edges of side plate metal | Check for chain interference, and repair as necessary to remove peeping marks.
53 | mechanical | chain drives | Wear on chain link plates or sides of sprocket teeth | Misalignment of the drive chain | Remove the chain, and correct the alignment of the sprockets and shafts.
53 | mechanical | chain drives | Broken pins, bushings, or rollers | Chain speed too high for the pitch and sprocket size | Check the number of sprocket teeth to ensure that it is within the recommended limits for the speed involved; Use a shorter pitch chain of equal or greater strength; Select a sprocket with more teeth, if necessary.
53 | mechanical | chain drives | Broken pins, bushings, or rollers | Material buildup in sprocket tooth pockets | Remove material buildup from the sprockets.
53 | mechanical | chain drives | Broken pins, bushings, or rollers | Heavy shock or suddenly applied loads | Reduce the shock loads.
54 | mechanical | chain drives | Broken pins. bushings, or rollers (continued) |  | Check the shaft runout for eccentricity paying particular attention to the locking device on the sprocket hub;The locking device can draw the hub off-center if there is a loose fit on the shaft
54 | mechanical | chain drives | Broken pins. bushings, or rollers (continued) | Inadequate lubrication | Lubricate the chain correctly-
54 | mechanical | chain drives | Broken pins. bushings, or rollers (continued) | Poorly fitted sprockets | Check the Sprockes for wear, and correct the bottom diameter.
54 | mechanical | chain drives | Broken pins. bushings, or rollers (continued) | Chain or sprocket corrosion | Remove any corrosion from the chain or sprocket, lubricate the chain correctly, and protect the chain and sprocke from further corrosion by keeping the chain clean and well lubricated.
55 | mechanical | chain drives | Pulsation | Chain tension too low | Adjust the take-ups to restore the proper tension.
55 | mechanical | chain drives | Pulsation | Chain speed too slow | Increase the size of the sprocket, or increase the conveyor Speed.
55 | mechanical | chain drives | Pulsation | Obstruction | Remove the obstruction, and ensure that the lower strand is not striking a foreign object.
55 | mechanical | chain drives | Pulsation | Heavy or tacky lubricants | Clean and lubricate the chain correctly.
55 | mechanical | chain drives | Pulsation | Sprockets with too few teeth, causing a large amount of chordal action | Replace with sprockets having the correct number of teeth.
55 | mechanical | chain drives | Pulsation | Eccentricity | Correct eccentricity ofhub hole.
56 | mechanical | chain drives | Broken sprocket teeth | Obstruction striking the cotter pins | Check the chain and sprocket clearances; Remove any foreign materials.
56 | mechanical | chain drives | Broken sprocket teeth | Excessive shock loads, especially with small, cast-iron sprockets | Reduce excessive shock loads, or change to steel Sprockets.
56 | mechanical | chain drives | Cotter pins coming out | Obstructions striking the cotter pins | Eliminate the obstruction; Tap the ends back until the cotter pin fits snugly against the side plates, or use a riveted chain.
56 | mechanical | chain drives | Cotter pins coming out | Cotter pins not installed properly, not spread apart and drawn back snugly against the side plates. | Correct the faulty installation.
57 | mechanical | chain drives | Damaged conveyed articles | Bent or damaged flights, attachments, or links | Repair or replace the damaged parts.
57 | mechanical | chain drives | Damaged conveyed articles | Obstruction in throughways or casings | Remove the obstruction.
57 | mechanical | chain drives | Damaged conveyed articles | Improper timing | Check timing sequence, chain elongation, and chain selection.
58 | mechanical | gear boxes | Noisy operation of the unit | Misalignment | Check the alignment of the unit; Check the condition of the coupling; If misalignment is the problem, have the maintenance group perform an alignment of the shafts.
58 | mechanical | gear boxes | Noisy operation of the unit | Faulty lubrication | Check oil level; Add lubricant if needed; Determine if lubricant is correct grade; If the lubricant is not the correct grade, replace with the correct lubricant.
58 | mechanical | gear boxes | Noisy operation of the unit | Excessive tension on the belts or the chain | Check the tension and the alignment of the drive auxiliaries, and relieve the tension if required
58 | mechanical | gear boxes | Noisy operation of the unit | Worn parts | Adjust or replace the worn parts.
58 | mechanical | gear boxes | Noisy operation of the unit | Overloading | Reduce the load.
59 | mechanical | gear boxes | Excessive operating temperature | Incorrect lubricant | Check the lubricant against the specification instructions; Replace with the correct lubricant.
59 | mechanical | gear boxes | Excessive operating temperature | Incorrect amount of lubricant | Check the level in the sight glass, and fill to the correct level; Ensure that the air breather is clean and functioning properly.
59 | mechanical | gear boxes | Excessive operating temperature | Overloading | Reduce the load.
59 | mechanical | gear boxes | Excessive operating temperature | Obstructed air flow | Check the air supply for proper fan circulation; Remove any obstructions; Avoid any high surrounding ambient temperatures; If the ambient temperature is high because of a local heat source, place some form of barrier between the heat source and the machine.
60 | mechanical | gear boxes | Oil leakage | Too much oil in the unit | Recheck the oil level with the unit shut down; Remove any excess oil.
60 | mechanical | gear boxes | Oil leakage | Clogged air breather | Remove the breather, and clean it.
60 | mechanical | gear boxes | Oil leakage | Loose bolts and nuts in jointed areas | Tighten all of the joints and end cap bolts.
60 | mechanical | gear boxes | Loosened mounting bolts | Vibration from fluctuating loads or misalignment | Check and realign the system; Tighten all of the bolts.
61 | mechanical | Lubricating Oil Systems | System pressure too low | Open drain-back valve from pressure line to return line | Close the pump relief valves.
61 | mechanical | Lubricating Oil Systems | System pressure too low | Pump relief valve or system pressure control valve set low | Check pump relief valves and the pressure control valve for normal Operation; Adjust as needed.
61 | mechanical | Lubricating Oil Systems | System pressure too low | Oil leak(s) in the system | Check for an oil leak; Repair as necessary.
61 | mechanical | Lubricating Oil Systems | System pressure too high | System pressure control valve set too high or not functioning properly | Check the system control valve, and adjust as needed.
61 | mechanical | Lubricating Oil Systems | System pressure too high | Plugged flow nozzle(s) | Check the flow controls for proper settings and positive indication of flow; Adjust the setting as necessary.
62 | mechanical | Lubricating Oil Systems | System pressure constantly fluctuating | System pressure control valve not functioning properly | Adjust the system pressure control valve to maintain a constant system pressure.
63 | mechanical | Lubricating Oil Systems | Very erratic pressures and sight flows, indicating a very uneven and burpy flow | Air being drawn into the system and pumped with the oil | Check the oil level in the reservoir and the free- floating operation of the floating suction; Verify there are no obstructions causing flowing suction to stick; Remove any debris from operation area; Check the suction line and the strainer to the pump for a possible air leak; Check the pressure tanks; If the tank is empty of oil, air may be leaking into the system from the air connection; Add oil as necessary.
63 | mechanical | Lubricating Oil Systems | Sounding of alarm | Dirty filter | Purge any air from the filter casing before changing over to the standby filter to put it into service.
63 | mechanical | Lubricating Oil Systems | Sounding of alarm | high differential pressure across the filter | Purge any air from the filter casing before changing over to the standby filter to put it into service.
64 | mechanical | Lubricating Oil Systems | Standby pump and alarm cycling on and off | Operating pump not running | Change the pump selector switch to reverse pumps; If the system now runs normally, investigate the pump taken out of service for a problem, such as a broken shaft.
64 | mechanical | Lubricating Oil Systems | Standby pump and alarm cycling on and off | Mercoid switches incorrectly set | Set the standby Mercoid switch approximately 5 and 15 psi below the desired system pressure.
64 | mechanical | Lubricating Oil Systems | Standby pump and alarm cycling on and off | Increased demand for oil from the system due to an oil leak | Look for oil leaks or some drastic change causing increased oil flow.
64 | mechanical | Lubricating Oil Systems | Standby pump and alarm cycling on and off | Oil temperature too high | Check that oil temperature on discharge side of cooler is within 10 °F of operational temperature; If it is not, make adjustments accordingly.
65 | mechanical | Lubricating Oil Systems | Pump running noisily | Low fluid level | Adjust the fluid supply to the pump.
65 | mechanical | Lubricating Oil Systems | Pump running noisily | System pressure too high | Adjust the pressure-relief valve to lower the pressure.
65 | mechanical | Lubricating Oil Systems | Pump running noisily | Variable-volume or pressure-compensated pump adjusted for too much flow | Adjust the pump.
65 | mechanical | Lubricating Oil Systems | Pump running noisily | Intake leaking | Locate and correct the leak
65 | mechanical | Lubricating Oil Systems | Pump running noisily | Pump speed too high | Decrease the pump speed.
65 | mechanical | Lubricating Oil Systems | Pump running noisily | Motor and pump not aligned | Have maintenance align the motor and pump.
65 | mechanical | Lubricating Oil Systems | Pump running noisily | Restricted intake | Find obstruction; clear intake; clean suction filters.
65 | mechanical | Lubricating Oil Systems | Pump running noisily | Worn pump | Repair or replace the pump.
66 | mechanical | Lubricating Oil Systems | Pump running noisily (continued) | Cavitation caused by lack of net positive suction head (NPSH) or turbulence from sharp pipe bends irmnediately upstream of the pump suction. | Lower the suction temperature.
66 | mechanical | Lubricating Oil Systems | Pump running noisily (continued) | suction pressure lower than the corresponding saturation temperature | Lower the suction temperature.
66 | mechanical | Lubricating Oil Systems | Pump running noisily (continued) | Recirculation of fluid at the impeller vane exit area | Avoid discharge restrictions. Increase the clearance at exit tips of vanes; /Never/ install higher horsepower driver without redesigning discharge and suction piping.
67 | mechanical | V-Belt Drives | Belt slipping | Not enough tension | Increase the tension. The deflection of the belt at midspan should be 1/64" for each inch of span between the centerlines of the driven and driving sheaves.
67 | mechanical | V-Belt Drives | Belt slipping | Drive overloaded | Increase the belt size.
67 | mechanical | V-Belt Drives | Belt slipping | Contaminants on belts or sheaves | Clean or change the belts or sheaves.
67 | mechanical | V-Belt Drives | Belt slipping | Heavy starting load | Increase the tension.
67 | mechanical | V-Belt Drives | Belt slipping | Not enough arc of contact | Lengthen the center distance, or use an idler.
68 | mechanical | V-Belt Drives | Belt turned over in sheave | Broken cords from prying belts on and off sheaves | Reduce the drive centers when you are installing the belts; Adjust the motor position to lessen the tension on the belts; Install new belts, and retention them.
68 | mechanical | V-Belt Drives | Belt turned over in sheave | Not enough tension | Increase the tension.
69 | mechanical | V-Belt Drives | Repeated belt breakage | Shock loads | Test the shaft runout for eccentricity; Have maintenance make repairs; Increase the tension or drive capacity.
69 | mechanical | V-Belt Drives | Repeated belt breakage | Broken cords from running or prying belts on and off sheaves | Reduce the drive centers when you are installing the belts; Adjust the motor position to lessen the tension on the belts; Install new belts, and retention them.
69 | mechanical | V-Belt Drives | Repeated belt breakage | Foreign objects falling into the sheaves | Provide protective guards.
70 | mechanical | V-Belt Drives | Rapid wear of the belt | Worn sheave grooves | Replace the sheaves.
70 | mechanical | V-Belt Drives | Rapid wear of the belt | Sheave diameter too small | Increase the sheave diameter.
70 | mechanical | V-Belt Drives | Rapid wear of the belt | Misalignment | Align the drive.
70 | mechanical | V-Belt Drives | Rapid wear of the belt | Drive overloaded | Increase the drive capacity.
70 | mechanical | V-Belt Drives | Rapid wear of the belt | Belts rubbing | Provide the correct running clearance.
70 | mechanical | V-Belt Drives | Rapid wear of the belt | Contaminated environment | Clean and protect the belts.
71 | mechanical | V-Belt Drives | Belt cracked and hardened, causing slippage | Excessive heat | Track down and eliminate the heat source; Provide ventilation.
71 | mechanical | V-Belt Drives | Belt whipping | Drive centers too long | Reduce the drive centers, or provide an idler.
71 | mechanical | V-Belt Drives | Belt whipping | Tensioner idler sheave out of adjustment | Reduce the drive centers, or provide an idler.
71 | mechanical | V-Belt Drives | Hot bearings | Inadequate bearing lubrication | lubricate the bearing.
71 | mechanical | V-Belt Drives | Hot bearings | Too much bearing lubricant | Open the vent/drain plug, and purge the lubricant cavity with fresh lubricant; Leave the vent open for approximately 30 minutes, and then close it
72 | mechanical | V-Belt Drives | Hot bearings (continued) | Drive belts too tight | Adjust the belt tension. The deflection of the belt at midspan should be 1/64" for each inch of span between the centerlines of the driven and driving sheaves.
73 | mechanical | V-Belt Drives | One or two belts broken in a set | Not a matched set of drive belts | Replace the drive belts with matching belts.
73 | mechanical | V-Belt Drives | One or two belts broken in a set | Belts broken internally because of poor installation practices | Move the motor inwards to detension the belts, and replace with matching belts, using the proper installation procedure; /Caution/ Do not use different manufacturers' belts to make up a set; Always use belts from one manufacturer because manufacturing processes differ from one manufacturer to another.
74 | mechanical | V-Belt Drives | Excessive belt stretch | Improper amount of take-up since the initial belt installation | Replace all the belts.
74 | mechanical | V-Belt Drives | Excessive belt stretch | Overload on the drive belt | Reduce the overload, or install a larger drive system.
74 | mechanical | V-Belt Drives | Excessive belt stretch | Internal breaks in the belt | Replace the belt; /Caution/ Never use a pry bar to install the belt in the sheave because this breaks the inner fibers on the belt and can break the sidewalls of the sheave.
75 | mechanical | V-Belt Drives | Unequal belt stretch | Not a matching set of belts | Replace With matching belts.
75 | mechanical | V-Belt Drives | Unequal belt stretch | Unequal coefficient of friction | Check and adjust the alignment of the sheaves, and correct the tension.
75 | mechanical | V-Belt Drives | Unequal belt stretch | Nonparallel shafts | Check and adjust the alignment of the sheaves, and correct the tension.
75 | mechanical | V-Belt Drives | Unequal belt stretch | Internal and nonvisible breaks in belts | Replace the belts.
75 | mechanical | V-Belt Drives | Unequal belt stretch | Broken belt cords | Replace the belts.
75 | mechanical | V-Belt Drives | Unequal belt stretch | Worn grooves in sheaves | Replaee the sheaves.
76 | mechanical | V-Belt Drives | Belt separation | Small sheaves | Replace with properly sized sheaves.
76 | mechanical | V-Belt Drives | Belt separation | Excessive belt tension | Check and adjust the belt tension.
76 | mechanical | V-Belt Drives | Topside belt wear | Belt obstruction | Remove the obstruction.
76 | mechanical | V-Belt Drives | Topside belt wear | Turned over or twisted belt | Adjust and inspect the belt. Replace as required.
76 | mechanical | V-Belt Drives | Opening of the envelope seam on belt | Rubber solvent or oil on the belt | Clean and inspect the belt. Replace the belt as required.
77 | mechanical | V-Belt Drives | Abnormal envelope wear | Abrasive condition, worn sheaves, improper sheave angle, slip, exposed to chemical fumes, obstructions, or high heat | Check the belt for an abrasive condition or any of the conditions mentioned as a probable cause; Replace the belts as required.
77 | mechanical | V-Belt Drives | Belt soft or swollen | Rubber solvent or oil on the belt | Clean and inspect the belt; Replace the belt as required.
77 | mechanical | V-Belt Drives | Belt envelope hardening and cracking | Exposure to severe heat and/or chemical fumes | Clean and inspect the belt; Replace the belt as required.
78 | mechanical | Fan Systems | Fan output below SCFM | Total resistance on system higher than expected | Check whether any other fans are discharging into the same outlet as the fan having problems; This could be a design problem; Inform engineering for an evaluation.
78 | mechanical | Fan Systems | Fan output below SCFM | Dampers closed or partially closed | check to see whether any dampers have been accidentally closed; Open any dampers that should be open.
78 | mechanical | Fan Systems | Fan output below SCFM | Speed too slow | Check the drive belts for slippage; Adjust the tension if the belts are not damaged; Ensure there is adequate lubrication to bearings; Have the electricians check out the motor.
79 | mechanical | Fan Systems | Fan output below SCFM (continued) | Dampers or variable inlet vanes incorrectly set | Readjust the damper control linkage turnbuckles to the calibrated setpoints.
79 | mechanical | Fan Systems | Fan output below SCFM (continued) | Poor fan inlet conditions, such as choked filters. | Check the pressure differential across the filters, and clean or replace the dirty filters.
79 | mechanical | Fan Systems | Fan output below SCFM (continued) | Atmospheric air induction through ducting leaks | Walk ducting system down, and check for leaks; An ultrasonic leak detector is an ideal tool to determine exactly where leaks occur.
79 | mechanical | Fan Systems | Fan output below SCFM (continued) | Fan rotation wrong | Ensure that the belt drive is not crossed. Have the electricians check the rotation of the motor.
79 | mechanical | Fan Systems | Fan output below SCFM (continued) | Wheel mounted backward on the shaft | Stop the fan, and have maintenance reverse the wheel.
80 | mechanical | Fan Systems | Vibration and noise | Unbalance due to dirt buildup on fan blades | Perform Vibration analysis to determine the magnitude of the problem, and then balance the fan; Water wash the fan blades to remove the buildup of dirt; If the fan operates in a boiler exhaust system or some other high temperature gaseous system, descale the blades.
80 | mechanical | Fan Systems | Vibration and noise | Poor foundations or warped baseplate | Check the foundations for cracks and breakage; Report the findings to engineering for resolution.
81 | mechanical | Fan Systems | Vibration and noise (continued) | Misalignment | Perform vibration analysis to determine the magnitude of the problem, and then align the fan shafts.
81 | mechanical | Fan Systems | Vibration and noise (continued) | Soft-foot conditions | Perform a soft-foot check on all the feet of the unit to determine if a soft-foot condition is the problem; Add or remove shims to correct condition.
81 | mechanical | Fan Systems | Vibration and noise (continued) | No zero cold-spring of ductwork at the fan connecfion | Check for ducting distortion if no expansion or flex joint is fitted; Adjust the hangers as needed.
82 | mechanical | Fan Systems | Damaged bearings | Belt drive misalignment | Ensure that the sheaves are the same width and are properly aligned with each other.
82 | mechanical | Fan Systems | Damaged bearings | Bad lubrication | Ensure that the correct lubricant is being used and that the bearings are vented during the lubricant application.
83 | mechanical | Fan Systems | Damaged bearings (continued) |  | Ensure that the bearing installation practices are correct.
83 | mechanical | Fan Systems | Damaged bearings (continued) | Bent shalt | When the fan is off, ensure that the unit is tumed to change the resting point periodically to prevent the shaft from sagging due to its own weight; Check the bearing mounts for undue stress due to bad foundations and misaligned ductwork.
84 | mechanical | Fan Systems | Damaged bearings (continued) | Misaligned belt drives | Ensure that the belts are sitting in the correct sheaves and are aligned to run true in the V-grooves; Check the lineup of the sidewalls of the sheaves with a straightedge or a stretched string.
85 | mechanical | Fan Systems | Damaged bearings (continued) | Worn coupling | Conduct a vibration analysis to determine whether the coupling is worn; The wrong grade of lubricant may have been used and accumulated in one spot, causing an unbalanced condition.
85 | mechanical | Fan Systems | Damaged bearings (continued) | Resonance effect from another machine(s) | Perform an evaluation to determine the extent of resonance and to track down the excitation source(s); To temporarily stop resonance-induced vibration, alter the mass of the unit by placing some weight, such as a bag of sand, on the unit.
85 | mechanical | Fan Systems | Damaged bearings (continued) | Fan rotating in wrong direction | Have electricians check the motor rotation and correct the rotation as required.
86 | mechanical | Fan Systems | Damaged bearings (continued) | Partial offset restriction on inlet side of fan, causing it to unload | Ensure that no foreign objects are causing a partial blockage on the inlet side of the fan; As fan blades turn past the obstruction, they will be unable to carry the full load and deflect.
86 | mechanical | Fan Systems | Bearing overheating | Overlubrication of bearing | Determine the capacity of the bearing, and follow the manufacturer's recommendations for lubrication.
86 | mechanical | Fan Systems | Bearing overheating | Misalignment | Ensure that the belts are sitting in the correct sheaves and are aligned to run true in the V-grooves; Check the lineup of the sidewalls of the sheaves with a straightedge or a stretched string.
87 | mechanical | Fan Systems | Bearings overheating (continued) | Unbalance | Rotate the shaft, and let it roll until it comes to rest on its own to check for static unbalance; Static unbalance can be corrected by hanging an appropriate weight opposite the resting, 6 o'clock position; Engineers who have the proper instrumentation should do more complex balance correction.
87 | mechanical | Fan Systems | Bearings overheating (continued) | Bent shaft | When the fan is off, make sure the unit is turned off the resting point periodically to prevent the shaft from sagging due to its owm weight; Check for undue stress on bearing mounts because of bad foundations and misaligned ductwork.
88 | mechanical | Fan Systems | Bearings overheating (continued) | Over-tensioned belts | Depress the belts at midspan, and measure the deflection to test the belt tension; The deflection should be equal to 1/64" per inch of span between the centers of the driven and driver units.
88 | mechanical | Fan Systems | Bearings overheating (continued) | Abnormal axial thrusting caused by misaligned belts | This can be cause by gross misalignment between the driver and the driven units; It can also be caused when one sheave is wider than the other one; To correct either one, align the belts to the center of the V in each sheave.
89 | mechanical | Fan Systems | Bearings overheating (continued) | Sheaves that have eccentric bores due to poor machining practices or cast with boss off-center | Plug the bore, and remachine it true; Eccentric bores cause the sheaves to turn off center, causing the belts to tension and detension each revolution; This continual jerking back and forth causes the bearings to take a terrible pounding; Keys and setscrews can have the same effect by drawing a sheave ofllcenter when the force is tightened.
90 | mechanical | Steam Traps | Trap blowing live steam | No prime, bucket, or traps because Trap not primed when originally installed | Prime the trap.
90 | mechanical | Steam Traps | Trap blowing live steam | No prime, bucket, or traps because Trap not primed after cleaned | Prime the cleaned trap.
91 | mechanical | Steam Traps | Trap blowing live steam (continued) | Bypass valve open or leaking | Remove or repair the bypass valve.
91 | mechanical | Steam Traps | Trap blowing live steam (continued) | Sudden pressure drop | Install a check valve ahead of the trap.
92 | mechanical | Steam Traps | Trap blowing live steam (continued) | Valve mechanism not closing because Scale or dirt lodged in orifice | Clean the trap.
92 | mechanical | Steam Traps | Trap blowing live steam (continued) | Worn or defective valve or disc mechanism | Repair or replace the defective parts.
92 | mechanical | Steam Traps | Trap blowing live steam (continued) | Ruptured bellows (thermostatic traps) | Replace the bellows.
93 | mechanical | Steam Traps | Trap blowing live steam (continued) | Back pressure too high in a thermodynamic trap because Worn or defective parts | Repair or replace the defective parts.
93 | mechanical | Steam Traps | Trap blowing live steam (continued) | Back pressure too high in a thermodynamic trap because Trap stuck open | Clean the trap.
93 | mechanical | Steam Traps | Trap blowing live steam (continued) | Back pressure too high in a thermodynamic trap because Undersized condensate return line or pig tank | Increase the line or pig tank size.
93 | mechanical | Steam Traps | Trap blowing live steam (continued) | Back pressure too high in a thermodynamic trap because Blowing flash steam caused by flash steam forming when the condensate is released to a lower or atmospheric pressure | No corrective action is required for this normal condition.
94 | mechanical | Steam Traps | Trap not discharging | Pressure too high because Trap rating too low | Install the correct size trap.
94 | mechanical | Steam Traps | Trap not discharging | Pressure too high because Orifice enlarged by normal wear | Replace the worn orifice.
94 | mechanical | Steam Traps | Trap not discharging | Pressure too high because Pressure-reducing valve set too high or broken | Readjust or replace the pressure-reducing valve; The valve may require a new diaphragm.
94 | mechanical | Steam Traps | Trap not discharging | Pressure too high because System pressure raised | Install the correct pressure change assembly.
95 | mechanical | Steam Traps | Trap not discharging (continued) | Condensate not reaching the trap because Strainer clogged | Blow out the screen with air, or replace it.
95 | mechanical | Steam Traps | Trap not discharging (continued) | Condensate not reaching the trap because Obstruction in the line to the trap | Remove the obstruction.
95 | mechanical | Steam Traps | Trap not discharging (continued) | Condensate not reaching the trap because Bypass valve opening or leaking | Remove or repair the bypass valve.
96 | mechanical | Steam Traps | Trap not discharging (continued) | Condensate not reaching the trap because Steam supply line shut off | Open the steam supply valve.
96 | mechanical | Steam Traps | Trap not discharging (continued) | Condensate not reaching the trap because Trap clogged with foreign matter | Clean the strainer, and reinstall it.
96 | mechanical | Steam Traps | Trap not discharging (continued) | Condensate not reaching the trap because Trap held closed by a defective mechanism | Repair or replace the defective mechanism.
96 | mechanical | Steam Traps | Trap not discharging (continued) | Condensate not reaching the trap because High vacuum in the condensate return line | Install the correct pressure change assembly.
97 | mechanical | Steam Traps | Trap not discharging (continued) | No pressure differential across the trap because Blocked or restricted condensate retum line | Remove the restriction.
97 | mechanical | Steam Traps | Trap not discharging (continued) | No pressure differential across the trap because Incorrect pressure change assembly | Install the correct pressure change assembly.
98 | mechanical | Steam Traps | Continuous discharge from trap | Trap too small and undersized for the capacity being handled | Install the proper size trap.
98 | mechanical | Steam Traps | Continuous discharge from trap | Trap pressure rating too high | Install the correct pressure change assembly.
98 | mechanical | Steam Traps | Continuous discharge from trap | Trap clogged | Clean the trap internals, and reinstall the strainer.
98 | mechanical | Steam Traps | Continuous discharge from trap | Strainer plugged | Clean the strainer.
98 | mechanical | Steam Traps | Continuous discharge from trap | Bellows overstressed in a themiostatic trap | Replace the bellows.
99 | mechanical | Steam Traps | Continuous discharge from trap | Loss of the prime | Install a check valve on the inlet side of the trap.
98 | mechanical | Steam Traps | Continuous discharge from trap | Failure of valve to seat due to worn valve and seat | Replace the wom parts.
99 | mechanical | Steam Traps | Continuous discharge from the trap (continued) | Scale and dirt deposits under the valve and in the orifice | Clean the trap.
99 | mechanical | Steam Traps | Continuous discharge from the trap (continued) | Worn guide pins and lever | Replace the worn parts.
99 | mechanical | Steam Traps | Sluggish or uneven heating | Capacity margin in trap for heavy starting loads | Install the proper size larger trap.
99 | mechanical | Steam Traps | Sluggish or uneven heating | Insufficient air handling capacity on bucket traps | Use thermic buckets, or increase the vent size.
99 | mechanical | Steam Traps | Sluggish or uneven heating | Short circuiting by using group traps | When steam traps are grouped, i.e. multiple traps are run into the same line, there is a possibility of condensate backup due to pressure inconsistencies or obstructions; Systems with many traps feeding into one return line are hard to troubleshoot because it is hard to determine which trap has the problem; Pipe traps individually from vessels.
100 | mechanical | Steam Traps | Sluggrsh or uneven heating (continued) | Inadequate steam supply due to pressure valve change | Restore normal steam pressure.
100 | mechanical | Steam Traps | Sluggrsh or uneven heating (continued) | Steam pressure-reducing valve setting off | Readjust or replace the reducing valve.
100 | mechanical | Steam Traps | Back pressure troubles | Condensate return line too small | Install a larger condensate return line.
100 | mechanical | Steam Traps | Back pressure troubles | Other traps blowing steam into header | Locate and repair other faulty traps.
100 | mechanical | Steam Traps | Back pressure troubles | Pig tank vent line plugged | Clean out pig tank vent line.
100 | mechanical | Steam Traps | Back pressure troubles | Obstruction in return line | Remove the obstruction.
100 | mechanical | Steam Traps | Back pressure troubles | Excess vacuum in return line | Install the correct pressure change assembly.
101 | electrical | Electric Motors | Motor not starting | Blown fuses | Replace with fuses that are at least 12% of the amperes listed on the nameplate.
101 | electrical | Electric Motors | Motor not starting | Overload trips | Check and reset the overload in the starter.
101 | electrical | Electric Motors | Motor not starting | Improper current supply | Verify that the current supplied matches the specifications on the motor nameplate and the load factor.
101 | electrical | Electric Motors | Motor not starting | Improper line connections | Check the connections, using the diagram supplied with the motor; If the wiring is connected improperly, have the electricians rewire it to the connection specified on the diagram.
102 | electrical | Electric Motors | Motor not starting (continued) | Open circuit in the winding or the starting switch | Have an electrician check for loose wiring connections; Verify that the starting switch inside the motor is closed. /Note:/ A humming sound when the switch is closed indicates an open circuit; Repulsion induction motors may spark at the brushes.
102 | electrical | Electric Motors | Motor not starting (continued) | Mechanical failure | Stop the motor, and ensure that the motor and drive turn freely; Check the bearings and lubrication; Add some lubricant to the bearings, and rotate the shaft slowly by hand; If it still feels rough, have the motor repaired by the maintenance group.
103 | electrical | Electric Motors | Motor not starting (continued) | Short-circuited stator | Have maintenance rewind the motor. /Note/ Blown fuses indicate short-circuited stator.
103 | electrical | Electric Motors | Motor not starting (continued) | Poor stator coil connection | Remove the end bell, and locate the connection problem, using a test lamp; if a fault is found, have the electricians repair it
103 | electrical | Electric Motors | Motor not starting (continued) | Defective rotor | Look for broken bars or end ring, Replace/repair
103 | electrical | Electric Motors | Motor not starting (continued) | Overloaded motor | Reduce the load.
103 | electrical | Electric Motors | Motor not starting (continued) | One phase of three-phase motor open | Check the lines for the open phase.
103 | electrical | Electric Motors | Motor not starting (continued) | Short-circuited stator | Have maintenance rewind the motor. /Note/ Blown fuses indicate short-circuited stator.
104 | electrical | Electric Motors | Motor not starting (continued) | Worn or sticking brushes on repulsion induction motors | Check for wear, and replace as necessary. Check for the correct brush pressure. Clean the commutator if it is dirty
104 | electrical | Electric Motors | Motor stalling | Wrong application | Verify that the type or size of motor is correct and is within the specified operational parameters; If the motor is not correct, an electrician should install a new motor that meets the specifications.
104 | electrical | Electric Motors | Motor stalling | Overloaded motor | Reduce the load.
104 | electrical | Electric Motors | Motor stalling | Low motor voltage | Ensure the nameplate voltage is restored and maintained.
104 | electrical | Electric Motors | Motor stalling | Open circuit due to blown fuses | Check overload relay, stator, and the push buttons to reset the fuses. Replace the fuses if necessary.
105 | electrical | Electric Motors | Motor stalling (continued) | Incorrect control resistance of wound motor | Check the control sequence Replace the broken resistors; Repair the open circuits.
105 | electrical | Electric Motors | Motor running and then dying down | Power failure | Have an electrician check for loose connections to the line, to the fuses, and to the control; Correctly tighten any loose connections that are found.
105 | electrical | Electric Motors | Motor not coming up to speed | Motor not properly sized for designed load of the system | Consult supplier for the proper type of motor, and replace the motor with the correctly sized unit.
105 | electrical | Electric Motors | Motor not coming up to speed | Voltage too low at motor terminals due to line drop | Use a higher voltage on the transformer terminals, or reduce the load.
105 | electrical | Electric Motors | Motor not coming up to speed | Improper control operation of the secondary resistance of the wound motor | Correct the secondary control.
106 | electrical | Electric Motors | Motor not coming up to Speed (continued) | Starting load too high | Check the load that the motor is supposed to carry at the start, and adjust as necessary.
106 | electrical | Electric Motors | Motor not coming up to Speed (continued) | Broken rotor bars | Look for cracks near the rings, and repair or replace as necessary; New rotor may be needed; Repairs are usually temporary.
106 | electrical | Electric Motors | Motor not coming up to Speed (continued) | Open prrmary crrcurt | Locate the fault, using a resting device.
106 | electrical | Electric Motors | Motor taking too long to accelerate | Excess loading | Reduce the load.
106 | electrical | Electric Motors | Motor taking too long to accelerate | Poor circuit | Check for high resistance; Have an electrician correct any deficiencies found; Refer to the manufacturer's manual for guidance.
106 | electrical | Electric Motors | Motor taking too long to accelerate | Defective squirrel-cage rotor | Replace With a new rotor.
107 | electrical | Electric Motors | Motor taking too long to accelerate (continued) | Applied voltage too low | Have the power company increase the power tap
107 | electrical | Electric Motors | Wrong rotation | Wrong sequence of phases | Reverse connections at motor or switchboard.
107 | electrical | Electric Motors | Motor overheating while running under load | Overload | Reduce the load.
107 | electrical | Electric Motors | Motor overheating while running under load | Wrong blowers or air shields that may be clogged with dirt, preventing the proper ventilation of the motor | Clean the blower or air shield. /Note/ A continuous stream of air leaving the motor indicates good ventilation; If this does not happen after cleaning, check with the manufacturer for advice; If the wrong blower or air shield is being used, the manufacturer may have to recommend a design change.
107 | electrical | Electric Motors | Motor overheating while running under load | One phase of motor open | Ensure that all of the leads are well connected.
108 | electrical | Electric Motors | Motor overheating while running under load (continued) | Grounded coil | Locate the fault and repair.
108 | electrical | Electric Motors | Motor overheating while running under load (continued) | Unbalanced terminal voltage | Check for faulty leads, connections, and transformers; and repair or replace as necessary.
108 | electrical | Electric Motors | Motor overheating while running under load (continued) | Shorted stator coil | Repair, and then check the wattmeter reading.
108 | electrical | Electric Motors | Motor overheating while running under load (continued) | High resistance | Have an electrician look for a faulty connection and correct the problem.
108 | electrical | Electric Motors | Motor overheating while running under load (continued) | High voltage | Have an electrician check the terminals of the motor, using a voltmeter; Make adjustments to lower the voltage.
109 | electrical | Electric Motors | Motor overheating while running under load (continued) | Low voltage | Have an electrician check the terminals of the motor, using a voltmeter; Make adjustments to raise the voltage.
109 | electrical | Electric Motors | Motor overheating while running under load (continued) | Rotor rubbing against the stator bore | Check the machining; If the rubbing is due to bad machining practices, replace the bearings.
110 | electrical | Electric Motors | Motor vibrates after corrections have been made | Motor misaligned | Realign the motor.
110 | electrical | Electric Motors | Motor vibrates after corrections have been made | Weak foundations | Strengthen the base.
110 | electrical | Electric Motors | Motor vibrates after corrections have been made | Coupling out of balance | Dynamically balance the coupling.
110 | electrical | Electric Motors | Motor vibrates after corrections have been made | Driven equipment out of balance | Dynamically balance the driven equipment.
110 | electrical | Electric Motors | Motor vibrates after corrections have been made | Bearings not in line | Line up the bearings properly.
110 | electrical | Electric Motors | Motor vibrates after corrections have been made | Defective ball bearing | Replace the bearing.
111 | electrical | Electric Motors | Motor vibrates after corrections have been made | Balancing weights shifted | Dynamically rebalance the rotor.
111 | electrical | Electric Motors | Motor vibrates after corrections have been made | Wound rotor coils replaced | Dynamically rebalance the rotor.
111 | electrical | Electric Motors | Motor vibrates after corrections have been made | Poly-phase motor running single-phase | Check for an Open circuit.
111 | electrical | Electric Motors | Motor vibrates after corrections have been made | Excessive end play | Adjust the bearing, or add a washer.
112 | electrical | Electric Motors | Unbalanced line current on poly-phase motors during normal Operation | Unequal terminal volts | Have an electrician check the leads and connections and adjust as necessary.
112 | electrical | Electric Motors | Unbalanced line current on poly-phase motors during normal Operation | Single-phase operation | Have an electrician check for open contacts.
112 | electrical | Electric Motors | Unbalanced line current on poly-phase motors during normal Operation | Poor rotor contacts in control wound rotor resistance | Have an electrician check the control devices; Correct the contacts.
112 | electrical | Electric Motors | Unbalanced line current on poly-phase motors during normal Operation | Brushes not in the proper position on the wound rotor | Ensure that the brushes are properly seated and the shunts are in good condition.
112 | electrical | Electric Motors | Scraping noise | Fan striking the insulation | Clear the fan.
112 | electrical | Electric Motors | Scraping noise | Fan rubbing against air shield | Remove the interference.
112 | electrical | Electric Motors | Scraping noise | Motor loose on the bedplate | Tighten the hold down bolts.
112 | electrical | Electric Motors | Noisy operation | Air gap not uniform | Check and correct the bracket fits or the bearing.
113 | electrical | Electric Motors | Noisy operation (continued) | Rotor unbalanced | Dynamically balance the rotor.
113 | electrical | Electric Motors | Hot bearings | Bent or sprung shaft | Straighten or replace the shaft.
113 | electrical | Electric Motors | Hot bearings | Excessive belt pull | Decrease the tension on the drive belts.
113 | electrical | Electric Motors | Hot bearings | Pulley too far from bearing | Move the pulley closer to the motor bearing.
113 | electrical | Electric Motors | Hot bearings | Pulley diameter too small | Replace with larger pulleys.
113 | electrical | Electric Motors | Hot bearings | Misalignment | Correct the misalignment; Realign the units
113 | electrical | Electric Motors | Hot sleeve bearings | Oil grooving in the bearing obstructed by dirt | Remove bracket or pedestal with bearing; Clean bearing housing and oil grooves; Replace oil.
113 | electrical | Electric Motors | Hot sleeve bearings | Oil viscosity too high | Use recommended lighter oil.
113 | electrical | Electric Motors | Hot sleeve bearings | Oil viscosity too low | Use recommended heavier oil.
114 | electrical | Electric Motors | Hot sleeve bearings (continued) | Too much end thrust | Reduce the thrust that is induced by the driver; Check the magnetic center of the motor.
114 | electrical | Electric Motors | Hot sleeve bearings (continued) | Badly worn bearing | Replace the defective bearing.
114 | electrical | Electric Motors | Hot anti-friction bearing | Insufficient lubricant | Maintain correct amount of lubricant in bearing.
114 | electrical | Electric Motors | Hot anti-friction bearing | Excess lubricant | Reduce the quantity of lubricant. /Note/ Reservoir should not be more than half full.
114 | electrical | Electric Motors | Hot anti-friction bearing | Deterioration of the grease or contaminated lubricant | Remove the old grease, wash the bearing thoroughly with kerosene, and replace with new grease.
114 | electrical | Electric Motors | Hot anti-friction bearing | Overloaded bearing | Check the alignment and the side and end thrusts.
114 | electrical | Electric Motors | Hot anti-friction bearing | Broken ball or rough races | Clean housing thoroughly; Replace the bearing.
115 | electrical | Electric Motors | Overload on the driver | Higher than design speeds | Check the diameter of the sheaves to ensure that they are correctly sized for the unit; Check the motor for the correct horsepower and loading; Clear any obstacles.
115 | electrical | Electric Motors | Overload on the driver | Belts rubbing hard against some projection | Check lubrication practices; Correct as required.
116 | electrical | Electric Motors | Overload on the driver (continued) | Poor lubrication | Collect a gas sample, and have engineering and chemistry check the gas analysis to determine the problem.
116 | electrical | Electric Motors | Overload on the driver (continued) | Density of gas too high | Ensure that the belt drive is not crossed; Have the electricians check the rotation of the motor.
116 | electrical | Electric Motors | Overload on the driver (continued) | Wrong rotational direction | When the fan is off, ensure that the unit is turned off the resting point periodically to prevent the shaft from‘sagging due to its own weight.
116 | electrical | Electric Motors | Overload on the driver (continued) | Bent shaft | Check for undue stress on the bearing mounts due to bad foundations and misaligned ductwork.
117 | electrical | Electric Motors | Overload on the driver (continued) | Misalignment | Ensure that the belts are sitting in their respective sheaves and are aligned to run true in the V-grooves; Check the lineup of sidewalls of the sheaves with a straightedge or a stretched suing; Have electricians check wiring; Check for overgreasing, especially on units that are greased by a pump grease gun.
117 | electrical | Electric Motors | Overload on the driver (continued) | Motor phases wrongly wired
117 | electrical | Electric Motors | Overload on the driver (continued) | Stator to air gap restricted | Check the motor that has only a pedestal bearing with the other end connected to the coupling. /Note/ The fan could be badly misaligned, which would affect the air gap between rotor and stator.
118 | electrical | Electric Motors | Overload on the driver (continued) | Broken or cracked rotor bars | Perform a vibration analysis; /Note/ This problem will require major work and may require a new rotor.
119 | electrical | Electric Motors (dc) | Excessive sparking or flashing at brushes | Rough commutator surface | Sand or turn down.
119 | electrical | Electric Motors (dc) | Excessive sparking or flashing at brushes | Low bar on commutator | Grind or turn down balance of commutator.
119 | electrical | Electric Motors (dc) | Excessive sparking or flashing at brushes | High bar on commutator | If extreme, lower with a mallet blow and tighten clamp rin;. Grind true.
119 | electrical | Electric Motors (dc) | Excessive sparking or flashing at brushes | High mica | Undercut.
119 | electrical | Electric Motors (dc) | Excessive sparking or flashing at brushes | Brushes too short | Replace with harder grade — if worn too soon — and not by a rough commutator.
119 | electrical | Electric Motors (dc) | Excessive sparking or flashing at brushes | Insufficient brush tension | Adjust.
119 | electrical | Electric Motors (dc) | Excessive sparking or flashing at brushes | Weak brush springs | Replace.
119 | electrical | Electric Motors (dc) | Excessive sparking or flashing at brushes | Brushes sticking in holders | Free them; Clean brushes if glazed.
120 | electrical | Electric Motors (dc) | Excessive sparking or flashing at brushes (continued) | Dirt or oil on commutator | Wipe clean. Clean brushes if glazed.
120 | electrical | Electric Motors (dc) | Excessive sparking or flashing at brushes. Blackened commutator. | Shortened armature winding | Test for a short. Do this after removing metallic contact between commutator bars. Repair armature.
120 | electrical | Electric Motors (dc) | Intermittent sparking at brushes | Open arrnature winding | Locate and replace bad coil — or repair defective joint.
120 | electrical | Electric Motors (dc) | Fine dust under coupling emploflng rubber buffers or pins | Misalignment | Realign set.
120 | electrical | Electric Motors (dc) | Smoke, or solder "Whiskers" extending from the armature | Over heating due to loose soldered connections that might cause future trouble | Ensure all connections are tight. Resolder all connections.
121 | electrical | Electric Motors (dc) | Motor will not start | Usually a line problem | Correct. Check source of power supply; Do not try to make the motor turn as it may burn up.
121 | electrical | Electric Motors (dc) | Motor will not start | Load too heavy; Disconnect motor to see if it starts without load | Reduce load - or replace motor with unit of greater capacity.
121 | electrical | Electric Motors (dc) | Excessive humming sound | Uneven air gap; Measure with feeler gauge | Replace bearings - before scraping noise indicates rotor is rubbing against stator.
121 | electrical | Electric Motors (dc) | Excessive humming sound | Unbalanced rotor or bent shaft. | Check balance of rotor on parallel bars; Check rotor TIR; Not to exceed +/- 0.002"
121 | electrical | Electric Motors (dc) | Regular clicking noise | Foreign matter in the air gap | Remove the rotor and clean.
121 | electrical | Electric Motors (dc) | Rapid knocking | Misalignment; Magnetic center out of location | Realign the set until knocking disappears; Reset the magnetic center.
122 | electrical | Electric Motors (dc) | Brush "chatter" | Extreme motor vibration | Determine source of vibration through analysis and correct problem.
122 | electrical | Electric Motors (dc) | Brush "chatter" | Vibration sources | Misalignment; Unbalance; Bent shaft; Resonance; Oil whirl
122 | electrical | Electric Motors (dc) | Vibration | Misalignment | Realign set
122 | electrical | Electric Motors (dc) | Vibration | Vibration in driven machine; Run motor disconnected for check | Eliminate source in machine, if possible. Or change to a flexible belt drive may be in order
122 | electrical | Electric Motors (dc) | Vibration | Rotor out of balance | Balance the rotor.
123 | electrical | Electric Motors (dc) | Motor overheating | Overload. | Compare nameplate rating; Check for excessive friction; Reduce load; Replace motor with one of a bigger capacity.
123 | electrical | Electric Motors (dc) | Motor overheating | Dirt in motor. | Ensure sufficient airflow across motor; Clean out dirt with a suitable solvent.
123 | electrical | Electric Motors (dc) | Motor overheating | Rotor rubbing on stator | Replace bearings.
123 | electrical | Electric Motors (dc) | Motor overheating | Shorted stator windings | Test with wattmeter and correct.
123 | electrical | Electric Motors (dc) | Motor overheating | Ground | Locate with a test lamp or growler and repair
124 | electrical | Electric Motors (dc) | Bearing overheating | Misalignment | Realign set.
124 | electrical | Electric Motors (dc) | Bearing overheating | Too much tension in chain or belt drive | Reduce tension using the following formula: Center span of belt deflection should be 1/64 inch per inch of centerline span between driver and driven units; Chain deflection should be 2% of centerline span.
124 | electrical | Electric Motors (dc) | Bearing overheating | Excessive end thrust | Reduce thrust from driver or machine; Ensure motor's magnetic center is correctly located.
124 | electrical | Electric Motors (dc) | Bearing overheating | Too much grease (ball or roller bearings) | Relieve supply to point set by the manufacturer.
124 | electrical | Electric Motors (dc) | Bearing overheating | Sticking oil slinger ring. | Clean, repair, or replace.
124 | electrical | Electric Motors (dc) | Bearing overheating | Insufficient lubricant | Add to point set by the manufacturer.
125 | electrical | Electric Motors (dc) | Commutator hot | Incorrect grade of brushes | Replace with the proper grade.
125 | electrical | Electric Motors (dc) | Commutator hot | Excessive brush pressure | Decrease the brush spring tension.
126 | electrical | Electrical Contacts | Overheating | Load current too high | Reduce the load; Use a larger contactor.
126 | electrical | Electrical Contacts | Overheating | Loose connections | Clean any discolored or dirty connections, and retighten them to the recommended torque setting.
126 | electrical | Electrical Contacts | Overheating | Overtravel and/or contact force too low | Adjust the overtravel as necessary; Replace the contacts, and replace the contact springs as required to correct any defects.
126 | electrical | Electrical Contacts | Overheating | Copper oxide or foreign matter collected on the contact faces | Clean the contact surfaces, using a fine file or sandpaper; /Note/ When performing this task in a dusty environment, use a dust-tight enclosure.
127 | electrical | Electrical Contacts | Overheating (continued) | Load on in excess of 8 hours | Change the operating procedure, and check with the factory for contacts more suitable for the length of use.
127 | electrical | Electrical Contacts | Overheating (continued) | Ambient temperature too high | Reduce the load; Provide better ventilation; Relocate the starter; Use a larger contactor.
127 | electrical | Electrical Contacts | Overheating (continued) | Line and/or load cables too small | Replace with line and cables that meet the proper NEC standards recommendation.
127 | electrical | Electrical Contacts | Welding of the contacts | Overtravel and/or contact force too low | Adjust the overtravel as necessary; Replace the contacts, and replace the contact springs as required to correct the defect.
127 | electrical | Electrical Contacts | Welding of the contacts | Contact bouncing on closing | Correct the coil overvoltage condition; Correct any mechanical defects.
128 | electrical | Electrical Contacts | Welding of the contacts (continued) | Poor contact alignment | Adjust contacts to touch simultaneously within 1/32" or to the manufacturer's specifications.
128 | electrical | Electrical Contacts | Welding of the contacts (continued) | Jogging duty too severe | Reduce the jogging cycle. Use a larger contactor.
128 | electrical | Electrical Contacts | Welding of the contacts (continued) | Excessive inrush current | Readjust the accelerating time or the operating sequence; Use a larger contactor.
128 | electrical | Electrical Contacts | Welding of the contacts (continued) | Vibration in the starter mounting | Insulate the starter from shock; Provide a more rigid support for the starter.
128 | electrical | Electrical Contacts | Shorter contact life | Low contact force | Adjust the overtravel, replace the contacts, replace the contact springs, and set them to the correct contact force as necessary.
128 | electrical | Electrical Contacts | Shorter contact life | Contact bouncing on opening or closing | Correct the coil overvoltage condition; Correct any mechanical defects.
129 | electrical | Electrical Contacts | Shorter contact life (continued) | Abrasive dust on the contacts | Clean and dress the contact faces in a dust-free environment. /Caution/ Do not use an emery cloth to clean and dress the contact faces; Use glasspaper or a diamond file.
129 | electrical | Electrical Contacts | Shorter contact life (continued) | Load current too high | Reduce the load; Use a larger contactor.
129 | electrical | Electrical Contacts | Shorter contact life (continued) | Jogging cycle too severe | Reduce the jogging cycle; Use a larger contactor.
129 | electrical | Electrical Contacts | Shorter contact life (continued) | Oil-immersed contactor being used instead of an air breaker contactor | Replace with an air breaker contactor; /Note/ An air breaker contactor may have 10 to 20 times longer contact life than an oil-immersed contactor of equal rating.
130 | electrical | Electric Molded Case Breakers | Frequent thermal nipping | Excessive current | The breaker may be operating properly and clearing an overload; Have an electrician check to see if the current is in excess of the thermal trip rating.
130 | electrical | Electric Molded Case Breakers | Frequent thermal nipping | Terminals improperly torqued to the base of the breaker | Visually inspect the breaker for discoloration that would indicate loose connections; Have electricians torque the connections to the correct setpoint.
131 | electrical | Electric Molded Case Breakers | Frequent thermal tripping (continued) | Cable improperly torqued in terminal | Visually inspect the breaker for discoloration that would indicate loose connections; Have the electricians check and correctly tighten the connections; /Note/ Machine vibrations can cause cables to loosen and can also cause cold flow when aluminum cables are used; Cold flow refers to the contraction of the aluminum when the line is cooling down after the load is removed; This shrinkage can sometimes cause the connections to loosen.
132 | electrical | Electric Molded Case Breakers | Frequent thermal tripping (continued) | Improper wire size | Replace with the correct size wire. /Note/ Since the cable acts as a heat sink and carries heat away from the breaker, the proper wire size is important.
132 | electrical | Electric Molded Case Breakers | Frequent thermal tripping (continued) | Ambient temperature too high | If the temperature fluctuates and frequently exceeds 140 °F, install an ambient compensating breaker.
133 | electrical | Electric Molded Case Breakers | Frequent thermal tripping (continued) | Trip unit improperly torqued to base | Remove the trip unit from the base, and inspect it for discoloration; Reinstall the trip unit, and torque it to the base in accordance with the designed settings that come with each unit. /Note/ A bright cherry red color indicates a temperature of approximately 1,45 0 °F for the trip unit; If the unit has experienced thermal damage, then it must be replaced.
133 | electrical | Electric Molded Case Breakers | Breaker tripping magnetically | High inrush current from the motor | Adjust the magnetic trip rating to the next higher setting or until the breaker does not trip when the motor is started.
134 | electrical | Electric Molded Case Breakers | Breaker tripping magnetically (continued) | Breaker tested with incorrect type of field testing | Retest, using a six-cycle impulse test. /Note/ A slow or gradual increase in current until the trip range is reached results in the breaker tripping at a lower value than that indicated on the trip unit; A six-cycle impulse test should be used; This is how the breakers are calibrated at the factory.
135 | electrical | Electric Molded Case Breakers | Breaker tripping magnetically (continued) | High peak current on Y~delta starter transfer during open transition | Close the open circuit; /Note/ If an open circuit happens during transfer, the peak current during transfer could exceed 20 times the full-load amperes; /Caution/ An extremely high magnetic trip setting can be supplied on the breaker, but the desired motor protection will be lost.
135 | electrical | Electric Molded Case Breakers | Mechanical and electrical malfunctions | High humidity | Remove the breakers from high humidity locations since high humidity can cause dielectric and other problems associated with moisture. Install heaters in the enclosure if the breakers cannot be removed l from the humidity
136 | electrical | Electric Molded Case Breakers | Mechanical and electrical malfunctions (continued) | Corrosive environment | Remove the breakers from corrosive environments if possible.
136 | electrical | Electric Molded Case Breakers | Mechanical and electrical malfunctions (continued) | Attachments not functioning correctly | Remove the cover from the breaker, and determine what type of attachment is fitted; Ensure that the attachment is functioning correctly; Ensure that the proper voltage is applied to an undervoltage release so that the breaker will operate when shunt trips are used; /Warning/ Ensure that the shunt trip is not energized while the operator is trying to close the breaker.
137 | electrical | Magnetic Circuit | Vibration and noise | Low frequency, high voltage, core clamps slackened off during shipment or handling | Adjust and secure the core clamps; If other problems exist, have a qualified electrician correct them.
137 | electrical | Magnetic Circuit | Overheating | High-input voltage | Adjust and secure the core clamps; If other problems exist, have a qualified electrician correct them.
137 | electrical | Magnetic Circuit | High exciting current | Low frequency, high-input voltage | Adjust and secure the core clamps; If other problems exist, have a qualified electrician correct them.
137 | electrical | Magnetic Circuit | High core loss | Low frequency, high-input voltage | Adjust and secure the core clamps; If other problems exist, have a qualified electrician correct them.
137 | electrical | Magnetic Circuit | Insulation failure | Very high core temperature due to high-input voltage or low frequency | Adjust and secure the core clamps; If other problems exist, have a qualified electrician correct them.
138 | electrical | Dielectric Circuit | Smoke | Insulation failure | Inform electrical maintenance.
138 | electrical | Dielectric Circuit | Burned insulation | Lightning surge | Have them correct the condition.
138 | electrical | Dielectric Circuit | Burned insulation | Broken terminals, taps, or arresters | Repair or replace as necessary.
138 | electrical | Dielectric Circuit | Burned insulation | Excessive dirt buildup or dust on the coils | Clean the coils.
138 | electrical | Dielectric Circuit | Overheating | Clogged air ducts | Clean the air ducts.
138 | electrical | Dielectric Circuit | Breakers or fuses open | Insulation failure | Replace the insulation; Reset the breakers or firses.