## Planilha1
pag | type | equipament | problem | cause | action
1 | mechanical | pumps | pump too hot and flashing off; pump churningup fluid and failing to discharge water after na initial surge and then continue to recirculate | unloading valve not working properly | repair or replace the unloading valve
1 | mechanical | pumps | pump too hot and flashing off; pump churningup fluid and failing to discharge water after na initial surge and then continue to recirculate | excessive wear in pump | repair or repplace the pump
1 | mechanical | pumps | pump too hot and flashing off; pump churningup fluid and failing to discharge water after na initial surge and then continue to recirculate | relif valve set too high | adjust the relief valve
1 | mechanical | pumps | pump too hot and flashing off; pump churningup fluid and failing to discharge water after na initial surge and then continue to recirculate | discharge valve throttled or closed | open the discharge valve
1 | mechanical | pumps | pump too hot and flashing off; pump churningup fluid and failing to discharge water after na initial surge and then continue to recirculate | leak in suction piipe; packing or seal worm | inspect the line for broken or loose connections to determine the source of the leak
2 | mechanical | pumps | pump churning up fluid and failing to discharge water after na initial surge and then continuing to recirculate (continued) | lift too great; discharge line blocked chocked up filter | report this as na engineering problem; it may require design changes; clean filters
2 | mechanical | pumps | pump churning up fluid and failing to discharge water after na initial surge and then continuing to recirculate (continued) | suction pipe too long | report this as na engineering problem; it may require design changes
2 | mechanical | pumps | pump churning up fluid and failing to discharge water after na initial surge and then continuing to recirculate (continued) | insufficient head; suction valve shut | increase the supply source level
2 | mechanical | pumps | pump churning up fluid and failing to discharge water after na initial surge and then continuing to recirculate (continued) | too much air in the system | check the suction system and glands for airs ingress; if the source is from a pound, check to see if there are any whirlpools sucking air into the system; throttle the pump to reduce the rate of withdraw from the supply source
3 | mechanical | pumps | heavy vibrations during the operation of the pump | pump and motor out of alignment; bem shaft; cavitation; recirculation; unusual wear | perform vibration analysis to determine the source of the problem(s); mechanical maintenance should conduct alignment checks and make the necessary adjustments
3 | mechanical | pumps | heavy vibrations during the operation of the pump | some rotating element broken off, causing na unbalanced condition | perform vibration analysis to determine the source of the problem; mechanical maintenance should conduct balancing corrections
4 | mechanical | pumps | heavy vibrations during the operation of the pump (continued) | cavitation from lack of net positive suction head or turbulence from sharp pipe bends immediately upstream of the pump; suction pressure lower than the corresponding saturation temperature | Lower the suction temperature.
4 | mechanical | pumps | heavy vibrations during the operation of the pump (continued) | Recirculation due to blocked or narrowed discharge line | Increase the clearance at the exit tips of vanes to eliminate and avoid discharge restrictions.
4 | mechanical | pumps | heavy vibrations during the operation of the pump (continued) | Obstruction lodged in one side of the impeller | Have maintenance open the pump casing and remove any obstruction that may be there; Check to ensure that there is no further damage.
5 | mechanical | pumps | Heavy vibrations during the operation of the pump (continued) | Lack of lubricant or over-lubrication | Inspect the oil well sight glasses, or check the dipsticks; Add lubricant as necessary; Detennine if the proper grade of lubricant is being used; Change the lubricant if necessary
5 | mechanical | pumps | Heavy vibrations during the operation of the pump (continued) | Pump not tumed regularly when sitting idle | The pump should be turned frequently when it is on standby to avoid false brinelling and other surface defects on bearings
5 | mechanical | pumps | Heavy vibrations during the operation of the pump (continued) | Incorrect installation | Contact mechanical maintenance to have the installation checked
6 | mechanical | pumps | Capacity or pressure of the pump reduced; Pump failing to deliver water | Wrong direction of rotation | Check the direction of the arrow that is usually cast on the casing to verify the rotation direction; Have electricians check the wiring connections and correct them
6 | mechanical | pumps | Capacity or pressure of the pump reduced; Pump failing to deliver water | Discharge line blocked | Check the direction of the arrow that is usually cast on the casing to verify the rotation direction; Have electricians check the wiring connections and correct them
6 | mechanical | pumps | Capacity or pressure of the pump reduced; Pump failing to deliver water | Discharge valve closed | Check the direction of the arrow that is usually cast on the casing to verify the rotation direction; Have electricians check the wiring connections and correct them
6 | mechanical | pumps | Capacity or pressure of the pump reduced; Pump failing to deliver water | Impeller mounted incorrectly | Have mechanical maintenance verify the impeller mounting and reverse the impeller on the shaft.
6 | mechanical | pumps | Capacity or pressure of the pump reduced; Pump failing to deliver water | Mechanical defects, such as worn rings, damaged impeller, or a defective casing gasket | Have maintenance verify and correct the problem
6 | mechanical | pumps | Capacity or pressure of the pump reduced; Pump failing to deliver water | Clogged filters | Check the pressure differential across the filter; If the differential is too high, change and clean filters
7 | mechanical | pumps | Motor using excessive power at rated temperature; Motor protection relay being tripped by pump | Required differential head or pressure lower than rated | Throttle the dischargevalve until the rated capacity is reached
8 | mechanical | pumps | Bearings running hot | Improper alignment | Perform Phase Angle analysis to determine piping misalignment; Perform soft-foot analysis; Cheek to see if correct grease is used and correct application; Determine if bearing was installed per manufacturer's procedure
8 | mechanical | pumps | Bearings running hot | Piping misalignment | Perform Phase Angle analysis to determine piping misalignment; Perform soft-foot analysis; Cheek to see if correct grease is used and correct application; Determine if bearing was installed per manufacturer's procedure
8 | mechanical | pumps | Bearings running hot | Bent shaft | Perform Phase Angle analysis to determine piping misalignment; Perform soft-foot analysis; Cheek to see if correct grease is used and correct application; Determine if bearing was installed per manufacturer's procedure
8 | mechanical | pumps | Bearings running hot | Poor lubrication | Perform Phase Angle analysis to determine piping misalignment; Perform soft-foot analysis; Cheek to see if correct grease is used and correct application; Determine if bearing was installed per manufacturer's procedure
8 | mechanical | pumps | Bearings running hot | Overgreasing | Perform Phase Angle analysis to determine piping misalignment; Perform soft-foot analysis; Cheek to see if correct grease is used and correct application; Determine if bearing was installed per manufacturer's procedure
8 | mechanical | pumps | Bearings running hot | Poor foundations | Perform Phase Angle analysis to determine piping misalignment; Perform soft-foot analysis; Cheek to see if correct grease is used and correct application; Determine if bearing was installed per manufacturer's procedure
8 | mechanical | pumps | Bearings running hot | Improperly fitted bearings | Perform Phase Angle analysis to determine piping misalignment; Perform soft-foot analysis; Cheek to see if correct grease is used and correct application; Determine if bearing was installed per manufacturer's procedure
9 | mechanical | pumps | Bearings waning hot (continued) | Bearing substitute used and never replaced with original specification model | Use the maintenance management tracking system to see if the bearing was replaced in an emergency with a substitute bearing because it was "close enough," and the substitute was never replaced with the correct one.
9 | mechanical | pumps | Insufficient discharge | Air leaks in suction line or stuffing box | Tighten the glands slightly; Check the suction line for leaks
9 | mechanical | pumps | Insufficient discharge | Wear rings worn or damaged | Replace wear rings; Determine correct wear ring clearances
9 | mechanical | pumps | Insufficient discharge | Foot valve too small | Determine the proper size of the foot valve.
10 | mechanical | pumps | Excessive power consumption; bent shaft | Speed too high | Determme the correct speed and specrfic gravrty or viscosity; A design change may be required
10 | mechanical | pumps | Excessive power consumption; bent shaft | Specific gravity or viscosity too high | Determme the correct speed and specrfic gravrty or viscosity; A design change may be required
10 | mechanical | pumps | Excessive power consumption; bent shaft | Bent shaft | Replace the shaft
10 | mechanical | pumps | Excessive power consumption; bent shaft | Rotating element binds | Remove the shaft and inspect
10 | mechanical | pumps | Excessive power consumption; bent shaft | Stuffing boxes too tight | Loosen the gland slightly if the stuffing box is too tight
10 | mechanical | pumps | Excessive power consumption; bent shaft | Wearing rings worn | Replace the rings
11 | mechanical | bearings | overhating | Wrong type of grease or oil causing breakdown of the lubricant | Consult with the lubricant manufacturer to verify correct grade of lubricant, and replace the old grease or oil with the correct one.
11 | mechanical | bearings | overhating | Low oil level | Add oil until the oil level is just below the center of the lowest ball or roller in the bearing
11 | mechanical | bearings | overhating | loss of oil through the seal | Add oil until the oil level is just below the center of the lowest ball or roller in the bearing
11 | mechanical | bearings | overhating | Housing overpacked with grease, causing excessive churning of the lubricant | Purge the bearing until only the lower half is 1/2 to 2/3 full of grease
11 | mechanical | bearings | overhating | Inadequate internal clearance from using substitute bearing | Replace with a bearing that meets the original design specification
12 | mechanical | bearings | overhating (continued) | Housing bore out of round | Determine what the true bore is and scrape the housing to relieve the pinching of the bearing
12 | mechanical | bearings | overhating (continued) | housing warped | Determine what the true bore is and scrape the housing to relieve the pinching of the bearing
12 | mechanical | bearings | overhating (continued) | Rotating seals rubbing against stationary parts | Check the running clearance of the rotating seal to eliminate the rubbing; Check the alignment of the bearing
12 | mechanical | bearings | overhating (continued) | Blocked oil return holes | Clean the holes. Investigate type of debris
12 | mechanical | bearings | overhating (continued) | Unbalanced load | Rebalance the machine; Replace the housing with one having the correct size bore
12 | mechanical | bearings | overhating (continued) | housing bore too large | Rebalance the machine; Replace the housing with one having the correct size bore
13 | mechanical | bearings | overhating (continued) | Incorrect oil level causing insufficient oil to reach the bearing | Clean the clogged holes to vent the oil gauge; Ensure bearing material is not the clogging agent; If it is, the bearing may have to be overhauled or replaced
13 | mechanical | bearings | overhating (continued) | Wrong type of lubricant, which has broken down and lost its lubricating properties | Check oil specs for the machine, and use the correct grade of lubricant.
14 | mechanical | bearings | Noisy bearing; Irregular Dents or Material Embedded in Raceways | Foreign matter such as dirt, sand, and carbon entering the bearing housing | Clean out the bearing housing. Replace any worn seals
14 | mechanical | bearings | Noisy bearing; Irregular Dents or Material Embedded in Raceways | Brinnelling | Rotate shafts 1/: turn in all stationary machines at least once per two weeks.
14 | mechanical | bearings | Noisy bearing; Irregular Dents or Material Embedded in Raceways | Static electrical arcing in the bearings | Ensure insulation and grounding gear is in good order.
15 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | Corrosive agents entering the bearing | Add a shroud or a finger to throw off any foreign matter.
15 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | Failure to remove foreign matter from the bearing housing before assembling the bearing unit | Carefully clean the housing, and always use fresh lubricant.
15 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | A flat on a ball or a roller due to skidding | Replace the bearing
16 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | Incorrectly mounted bearing | Replace the bearing without hammering any part of it; Use a press to install bearing or unifomily heat or chill bearing to set it
16 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | bearing hammered onto the shalt or into the housing | Replace the bearing without hammering any part of it; Use a press to install bearing or unifomily heat or chill bearing to set it
16 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | Interference of other movable parts of the machine | Check every moving part for interference; Reset the parts to provide the necessary clearance.
16 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | Unbalanced load | Rebalance the unit; Replace the housing with one that has the correct size bore.
16 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | housing bore too large | Rebalance the unit; Replace the housing with one that has the correct size bore.
16 | mechanical | bearings | Noisy bearing (continued); Irregular Dents or Material Embedded in Raceways | Bearing exposed to resonance-caused vibration while the machine is idle | Carefully examine the bearing for wear spots that are separated by the distance equal to the spacing of the balls; Replace the bearings
17 | mechanical | bearings | Vibration | Distortion of shaft and inner ring | Re-machine the shaft fillet to obtain the correct support.
17 | mechanical | bearings | Vibration | Distortion of the housing and outer ring, causing pinching of the bearing | Remachine the housig fillet to obtain the correct support; Check manufacturer's tolerance measurement guides.
17 | mechanical | bearings | Vibration | Rotating seals rubbing against the stationary parts | Check the running clearance of the rotating seals to eliminate rubbing
17 | mechanical | bearings | Vibration | Incorrectly mounted bearing as indicated by hammer blow signs on the bearing | Replace with a new bearing without hammering it into place; Follow the bearing manufacturer's fitting recommendations.
17 | mechanical | bearings | Vibration (continued) | Inadequate support in the housing, causing the outer ring to cock | Remachine the housing fillet to relieve stress; Re-machining may require a shoulder collar.
18 | mechanical | bearings | Vibration (continued) | General vibration of the machine | Check the balance of the machine; Rebalance the machine if necessary
18 | mechanical | bearings | Vibration (continued) | Shaft and housing shoulders and face of the locking nut not square with the bearing seat | Remachine the parts to obtain squareness; Ensure that there is a radius machined in at root of shoulder to minimize stress riser
19 | mechanical | bearings | Bearing loose on the shaft | Shaft diameter too small or adapter not tight enough | Metalhze the shaft, and regrmd it to obtain a proper fit; Retighten the adapter to get a firmer grip on the shaft
19 | mechanical | bearings | Bearing loose on the shaft | Knurling and center punching of the bearing seat on the shaft, causing the high spots to be flattened when the load is applied | Metallize and regrind the shafi to the proper size; Stress relieve shaft before putting it back into service
19 | mechanical | bearings | Bearing loose on the shaft | loose fitting shaft | Metallize and regrind the shafi to the proper size; Stress relieve shaft before putting it back into service
20 | mechanical | bearings | Shaft difficult to turn by hand | Inadequate shoulder support in the housing causing bending of the shaft | Remachine the shaft fillet to relieve the stress; This may require a shoulder collar to be fitted.
20 | mechanical | bearings | Shaft difficult to turn by hand | Distortion of the bearing seals | Remachine the housing shoulder to clear the seal.
20 | mechanical | bearings | Shaft difficult to turn by hand | Bearing seat diameter machined oversize, causing excessive expansion of the shaft and bearing inner ring, thus reducing the clearance in the bearing | Grind and hone the shaft to obtain a proper fit between the inner ring of the bearing and the shaft.
21 | mechanical | bearings | Shaft difficult to turn by hand | Incorrect linear or angular alignment of two or more coupled shafts with two or more bearings | Shim the pillow blocks to correct the alignment; Ensure that the shafts are coupled in a straight line;This is especially important when three or more bearings operate on one shaft
21 | mechanical | bearings | Shaft difficult to turn by hand | Distortion of the housing and the outer ring causing pinching of the bearing | Remachme the housing fillet to obtain the proper support.
21 | mechanical | bearings | ANGULAR MISALIGNMENT | Incorrect linear or angular alignment of two or more coupled shafts with two or more bearings | Shim the pillow blocks to correct the alignment; Ensure that the shafts are coupled in a straight line;This is especially important when three or more bearings operate on one shaft
21 | mechanical | bearings | ANGULAR MISALIGNMENT | Distortion of the housing and the outer ring causing pinching of the bearing | Remachme the housing fillet to obtain the proper support.
21 | mechanical | bearings | Frequent replacements | Unequal load distribution on the bearing | Rework the shaft, the housing, or both to obtain a proper fit; A new shaft may be required
22 | mechanical | bearings | Oil leakage | Air flowing over the bearings, for example, a forced draft fan with air inlet over the bearings | Provide adequate baffling to divert the direction of the airflow.
22 | mechanical | bearings | Oil leakage | Oil leakage at the housing split causing excessive loss of lubricant | Use a thin layer of gasket cement to seal off the leakage; Shut down the equipment if the leakage is excessive
22 | mechanical | bearings | Oil leakage | Failure to remove debris from the bearing housing before assembling the bearing unit | Always carefully clean the housing, and use fresh lubricant
23 | mechanical | valves | Valve gland leakage | Packing too loose | Tighten the packing enough to stop the leak.
23 | mechanical | valves | Valve gland leakage | Packing reached the end of its useful life | Repack the gland with new correct sized packing rings.
23 | mechanical | valves | Valve gland leakage | Insufficient number of turns of packing | Check the number of packing rings that should be in the gland. Repack the gland with sufficient turns.
23 | mechanical | valves | Valve gland leakage | Packing ring butts all in line | Stagger the ring butts by placing the first at O°the next at 180° and then a 90°-270°; Repeat the rotating sequence until the stuffing box is filled
23 | mechanical | valves | Valve gland leakage | Valve stem badly scored | Replace valve stem; Check why it is scored first
24 | mechanical | valves | Valve gland leakage (continued) | Wrong grade packing material | Replace with the correct grade.
24 | mechanical | valves | Valve gland leakage (continued) | Cocked gland follower | Adjust the gland follower to correctly place the follower at a 90° angle to the stem axis.
25 | mechanical | valves | Body to bonnet gasket leakage | Gasket beyond the 60% crush factor | Replace the gasket with a new one; Smear the gasket surfaces with a suitable lubricant to help preserve it.
25 | mechanical | valves | Body to bonnet gasket leakage | Wrong type of gasket material | Replace the gasket with a new one; Smear the gasket surfaces with a suitable lubricant to help preserve it.
25 | mechanical | valves | Body to bonnet gasket leakage | Hammer-cut gasket and fibers destroyed | Replace the gasket; Gaskets should always be cut with a circular cutter and holes put in using a belt punch.
26 | mechanical | valves | Body to bonnet gasket leakage (continued) | Wrong gasket material | Replace with the correct gasket material; The most expensive material is not always the best; Use the gasket material that is recommended for the application.
26 | mechanical | valves | Body to bonnet gasket leakage (continued) | Gasket landing surfaces dirty | Replace with the correct gasket material; The most expensive material is not always the best; Use the gasket material that is recommended for the application.
26 | mechanical | valves | Body to bonnet gasket leakage (continued) | Gasket landing grooved by wire-drawing | Replace with the correct gasket material; The most expensive material is not always the best; Use the gasket material that is recommended for the application.
26 | mechanical | valves | Body to bonnet gasket leakage (continued) | Scored body or bonnet seal faces | Machine finish the gasket landing faces, and maintains them in that condition; Scrape off any old gasket debris, and ensure that the surfaces are left clean.
26 | mechanical | valves | Body to bonnet gasket leakage (continued) | Body/or bonnet bolts improperly tightened | Torque the bolts down in a star pattern to ensure that the joint is squarely made.
27 | mechanical | valves | Body to bonnet gasket leakage (continued) | Gasket too old and pressure blown | Replace with a new gasket; New gaskets should always be used for replacements; Never reuse the old gasket.
28 | mechanical | valves | Gate valve difficult to operate | Packing gland too tight | Adjust the packing until the valve operates easily.
28 | mechanical | valves | Gate valve difficult to operate | Too many turns of packing installed | Check the drawing for the correct number of turns required, and adjust.
28 | mechanical | valves | Gate valve difficult to operate | Piping misalignment | Break the joint, and correctly realign the pipe to the valve; Align piping with zero cold spring .
28 | mechanical | valves | Gate valve difficult to operate | Bent valve stem | Straighten the stem to +/- 0.002" TIR max
28 | mechanical | valves | Gate valve difficult to operate | Wrong size handwheel or motor operator | Check the specifications, and replace with the proper handwheel.
29 | mechanical | valves | Gate valve hard to operate (continued) | Stern threads or nut damaged | Clean the threads, using thread chaser.
29 | mechanical | valves | Gate valve hard to operate (continued) | Thermal binding of valve closed | Contact maintenance; To prevent this problem from occurring, avoid forcing the valve into the seat in high temperature systems.
30 | mechanical | valves | Gate valve hard to operate (continued) | Piping misaligned | Avoid twisting valve body, especially check valves, gate valves and butterfly valves.
30 | mechanical | valves | Gate valve hard to operate (continued) | Valve internals out of alignment due to body stresses caused when piping 10 valve is misaligned | Avoid twisting valve body, especially check valves, gate valves and butterfly valves.
31 | mechanical | valves | Gate valve chattering | Valve being used to throttle flow | Adjust the valve to fully open or fully closed; Gate valves are not designed to control or throttle flow; Do not use them for this function.
31 | mechanical | valves | Gate valve chattering | Piping distortion due to loading or temperature distortion | Install spring hangers, and check the valve to the piping nozzle alignment; Piping to valve alignment should have zero-cold-spring; In other words, both connections should be perfectly aligned with each other with no stress.
32 | mechanical | valves | Gate valve chattering (continued) | Partially open valve | Open or shut the valve completely; The gate valve should always be fully open or shut.
32 | mechanical | valves | Gate valve chattering (continued) | Natural vibration frequency being excited by some other natural or induced vibration frequency | Change the mass by stiffening the valve; Add a weight to the pipe as close as possible to the valve.
32 | mechanical | valves | Gate valve chattering (continued) | Rising stem valve in confined space restricting full opening | Change the valve for a non-rising stem valve.
32 | mechanical | valves | Gate valve chattering (continued) | Stem lock nut on yoke loose | Tighten the yoke nut.
33 | mechanical | valves | Leakage across the disc and seat in a globe valve | Erosion across the seat face | \Caution\During throttling Operations, do not close the valve far enough to induce a high-pitched screaming noise.
33 | mechanical | valves | Leakage across the disc and seat in a globe valve | Reface the disc and seat, and lap to ensure good contact all around the faces. | \Caution\During throttling Operations, do not close the valve far enough to induce a high-pitched screaming noise.
33 | mechanical | valves | Leakage across the disc and seat in a globe valve | Seat contact surface area too wide | Machine the disc and seat to produce a very narrow contact band around the seat and disc faces; Ideally, maintain a 05° differential angle between the seat and disc faces.
33 | mechanical | valves | Leakage across the disc and seat in a globe valve | Incorrect valve in the system | Change the valve immediately if the valve israted at 200 WOG and 125 S and is operating in a 400-psi steam system.
34 | mechanical | valves | Leakage across the disc and seat in a globe valve (continued) | Incorrect valve in the system (continued) | \Warning\ If the valve is overpressurized, it is dangerous to operate at this pressure; It should be operating at no more than 200 psi in a water, oil, or gas system, and no more than 125 psi in steam system.
35 | mechanical | valves | Intermittent leakage across the valve | Disc cocking due to bent valve stem | Remove the stem, and check the TIR. Straighten the valve stem.
35 | mechanical | valves | Intermittent leakage across the valve | Disc sticking due to slightly ofi center misalignment of bonnet stem threads | Change the valve; Check piping alignment to the valve body; Piping should have zero cold spring with valve nozzle.
35 | mechanical | valves | Intermittent leakage across the valve | Stem attached to the disc nut is too tight, restricting the disc from self-centering in the seat | Add shims one at a time between the stem nut and disc shoulder until sufficient float is achieved.
36 | mechanical | valves | Screwed bonnet loosening off repeatedly | Valve back-seated too tightly | Retighten the bonnet lock nut; \Warning\ If this problem is not corrected, the valve may blow out and cause injury; To avoid this problem, do not force the stem to the backseat against the cover, particularly using a valve wrench.
37 | mechanical | valves | Screwed bonnet loosening off repeatedly (continued) | Missing lock screw or tab | Verify the need for a lock screw or tab by reading the drawing or manufacturer's documentation, and reinstall the tab or lock screw if necessary; \Warning\ Never install a screwed bonnet globe valve in a high-pressure system or a dangerous substance system because the bonnet can become unscrewed if it is forced against the backseat.
37 | mechanical | valves | Screwed bonnet loosening off repeatedly (continued) | Bonnet lock nut not torqued to specified setpoints | Verify the setting, using a torque wrench to correct the setting if required.
38 | mechanical | valves | Piping flange leaking | Bolts improperly tightened | Loosen the bolts, and retighten properly; Flange bolts need to be tightened sequentially around the bolt pitch circle; After the first nut is tightened snugly, go 180° across to the second nut, and tighten it snugly; Go 90° to the third nut, and tighten it snugly; Go 180° to tighten the fourth nut Repeat this sequence until all the bolts are snugly tightened; Torque all nuts to specification in the same sequence to complete the tightening process.
39 | mechanical | valves | Valve to piping flange leaking (continued) | Reusing old gasket, causing old gasket material to stick to the flange surface | Scrape the flange clean of all foreign material; Ensure that the flange faces are properly aligned to each other and at the zero coldvspring setpoint; Always use a new gasket when installing a valve or making repairs.
40 | mechanical | valves | Valve to piping flange leaking (continued) | Wrongly set Flexitallie gasket | If the compression is less than 60% and no other damage is apparent, then tighten the gasket to the correct setpoint. If the compression is greater than 60%, scrap the gasket, and replace it with a new gasket; flexitallic gasket corrugations must be compressed to a minimum of 60% of the original thickness for effective sealing. If the gasket is compressed beyond 90%, it becomes ineffective.
41 | mechanical | valves | Pressure safety valve leaking | Improper setting | Correct the setting, or contact maintenance; /Warning/ Ensure that a gag is not left in place or being used to try to stop leakage across valve seat; Pressure tests the valve to lift at 110 % of the working pressure of the boiler.
41 | mechanical | valves | Pressure safety valve leaking | Valve-disc-to-seat contact area too large, causing valve simmering to take place | Reface the seat face and disc face to maintain a 1/2 degree angle differential between the points of contact.
42 | mechanical | valves | Pressure safety valve leaking (continued) | Cracked or broken compression spring | Perform a visual inspection of the spring for cracks or breaks; If the spring can be taken off valve without being broken, hang it on a string, and strike it very lightly with a peen hammer; If the spring rings loudly and clearly, it does not have a crack; If the spring makes a clunking sound, it is cracked; Replace it.
42 | mechanical | valves | Pressure safety valve leaking (continued) | Bent valve stem | Check the stem TIR to ensure that the stem is not bent. Straighten the stem if necessary.
43 | mechanical | valves | intermittent vibration on valves and associated piping | Improper loading of pipe hangers | Evaluate the current setpoints to ensure that they meet specifications.
43 | mechanical | valves | intermittent vibration on valves and associated piping | Resonance | Remove anything that should not be on the piping; Piping and valves may be loaded down with scaffolding or maintenance walkways; This can alter the mass, affecting the natural frequency and causing the scaffolding or walkways to vibrate in tune with a pump or motor having the same natural frequency; This vibration can have devastating results.
43 | mechanical | valves | intermittent vibration on valves and associated piping | Water hammer | Ensure that the steam traps are operating and do not need maintenance; Clean the traps as necessary; Open the drain valves during any plant shutdown.
44 | mechanical | valves | Continual leakage across a butterfly valve | Valve may be installed in the wrong direction | Check the direction arrow casting on the side of valve body; Reverse the body installation if the directional arrow indicates that the valve is incorrectly installed.
44 | mechanical | valves | Continual leakage across a butterfly valve | Piping misalignment with valve | Inspect and report the findings to maintenance; Piping misalignment can distort the valve body and can cause the disc shaft trunnions to get out of alignment and bind up.
44 | mechanical | valves | Continual leakage across a butterfly valve | Neoprene valve seat and gasket | Check the valve seat to ensure that it did not kink or roll during installation; Straighten as necessary.
45 | mechanical | valves | hand-operated valve difficult to open | Thread damage | Take the stem out of the valve. and run a die-nut down the thread if it is a standard thread; If it is an Acme thread, use a thread chaser or a fine file to remove any imperfections.
45 | mechanical | valves | hand-operated valve difficult to open | Shaft bent | Remove the shaft, and check TIR; Straighten the shaft, and reinstall in the valve.
45 | mechanical | valves | hand-operated valve difficult to open | Valve body twisted | Separate the pipe from the valve, and observe how far the pipe moves out of alignment; if the pipe is out of alignment, the pipe must be bent until it meets the valve nozzle with zero cold spring; /Warning/ If a hand-operated valve cannot be moved without difficulty, it requires maintenance; Never force a valve by using a wrench.
45 | mechanical | valves | hand-operated valve difficult to open | piping misaligned to valve body | Separate the pipe from the valve, and observe how far the pipe moves out of alignment; if the pipe is out of alignment, the pipe must be bent until it meets the valve nozzle with zero cold spring; /Warning/ If a hand-operated valve cannot be moved without difficulty, it requires maintenance; Never force a valve by using a wrench.
46 | mechanical | valves | Hand-operated valve difficult to open | Bonnet stem nut out of alignment with valve seat | Contact maintenance and the machineshop to correct this problem and replace the valve.
46 | mechanical | valves | Hand-operated valve difficult to open | Gland packing too tight | Slacken off the gland follower, and allow the packing to move slightly.
46 | mechanical | valves | Hand-operated valve difficult to open | Gland packing badly installed | Repack the valve.
47 | mechanical | chain drives | Noisy drive | Incorrect tension | Check the slack side span for 2% deflection, and adjust the chain tension as necessary.
47 | mechanical | chain drives | Noisy drive | Insufficient lubrication | Check the drive for proper lubrication; Lubricate the drive as necessary.
47 | mechanical | chain drives | Noisy drive | Worn drive | Check the chain and sprocket for wear, and have it replaced if worn.
47 | mechanical | chain drives | Noisy drive | Misalignment of sprockets | Check the alignment, and realign as necessary.
47 | mechanical | chain drives | Noisy drive | Loose casing or bearings | Draw up all bolts, and brace the casings as required.
47 | mechanical | chain drives | Noisy drive | Pitch too large | Check chain drive spec chart; Change the chain.
48 | mechanical | chain drives | Chain climbing sprocket teeth | Chain worn | Check for chain wear. Replace chain as necessary.
48 | mechanical | chain drives | Chain climbing sprocket teeth | Insufficient tension | Check chain tension. Increase tension as needed.
48 | mechanical | chain drives | Chain climbing sprocket teeth | Material in tooth pockets | Clean sprocket. Eliminate cause of material buildup.
48 | mechanical | chain drives | Chain climbing sprocket teeth | Chains & sprockets fit poorly | Notify the maintenance department.
48 | mechanical | chain drives | Chain climbing sprocket teeth | Insufficient chain wrap | Change the driver arrangement to get more sprocket-teeth in contact with the chain, or use an idler take-up sprocket to increase the wrap.
48 | mechanical | chain drives | Chain climbing sprocket teeth | Excessive chain slack | Adjust the centers or take-up sprockets for a 2% final deflection.
49 | mechanical | chain drives | Drive is running excessrvely hot | Running too fast | Check drive for proper speed. Adjust as required.
49 | mechanical | chain drives | Drive is running excessrvely hot | Insufficient lubrication | Check for the correct type and amount of lubricant.
49 | mechanical | chain drives | Drive is running excessrvely hot | Chain operating too fast for bath lubrication | Use the oil stream system to lubricate the chain.
49 | mechanical | chain drives | Drive is running excessrvely hot | Chain immersed too deeply in oil bath in bath-lubricated drive | Check the drive for obstructions, and check the guard design; Remove all obstructions.
50 | mechanical | chain drives | Chain hanging in sprocket | Wont sprocket teeth | Check for chain wear, and replace the chain as necessary.
50 | mechanical | chain drives | Chain hanging in sprocket | Material buildup on driver sprocket tooth pockets | Clean and lubricate the sprockets correctly.
50 | mechanical | chain drives | Chain hanging in sprocket | Sticky lubricant | Check the grade of the lubricant, and refer to the lubricant chart for that particular chain drive configuration; Replace with the recommended lubricant as necessary.
51 | mechanical | chain drives | Chain whip | Insufficient tension | Correct the tension; The tension should be set to deflect 2% of the pitch between the driver and the driven sprockets.
51 | mechanical | chain drives | Chain whip | Stiff chain joints | Replace the bad joints, or install a new chain.
51 | mechanical | chain drives | Chain whip | Excessive chain slack | Install a chain take-up or idler sprocket, or adjust the centers of the sprockets.
51 | mechanical | chain drives | Chain whip | High pulsating loads | Reduce the load where possible, or replace the chain with one of suitable length.
51 | mechanical | chain drives | Chain whip | Nonuniforrn chain wear | Investigate why the chain is wearing in an irregular manner; Replace the chain.
52 | mechanical | chain drives | Stiff chain joints | Misalignment of drive | Have maintenance check the alignment and correct as necessary.
52 | mechanical | chain drives | Stiff chain joints | Worn and corroded chain | Replace the chain; Provide the correct lubrication
52 | mechanical | chain drives | Stiff chain joints | Inadequate lubrication | Clean and lubricate the chain correctly; Refer to the lube manual for correct lubricant and application.
52 | mechanical | chain drives | Stiff chain joints | Corrosion on the chain | Remove any corrosion, lubricate the chain correctly, and protect the chain from further corrosion by keeping it clean and well lubricated.
52 | mechanical | chain drives | Stiff chain joints | Excessive overload | Identify the overload cause, and reduce it.
52 | mechanical | chain drives | Stiff chain joints | Material buildup in joints | Clean and lubricate the chain more frequently.
52 | mechanical | chain drives | Stiff chain joints | Peening edges of side plate metal | Check for chain interference, and repair as necessary to remove peeping marks.
53 | mechanical | chain drives | Wear on chain link plates or sides of sprocket teeth | Misalignment of the drive chain | Remove the chain, and correct the alignment of the sprockets and shafts.
53 | mechanical | chain drives | Broken pins, bushings, or rollers | Chain speed too high for the pitch and sprocket size | Check the number of sprocket teeth to ensure that it is within the recommended limits for the speed involved; Use a shorter pitch chain of equal or greater strength; Select a sprocket with more teeth, if necessary.
53 | mechanical | chain drives | Broken pins, bushings, or rollers | Material buildup in sprocket tooth pockets | Remove material buildup from the sprockets.
53 | mechanical | chain drives | Broken pins, bushings, or rollers | Heavy shock or suddenly applied loads | Reduce the shock loads.
54 | mechanical | chain drives | Broken pins. bushings, or rollers (continued) |  | Check the shaft runout for eccentricity paying particular attention to the locking device on the sprocket hub;The locking device can draw the hub off-center if there is a loose fit on the shaft
54 | mechanical | chain drives | Broken pins. bushings, or rollers (continued) | Inadequate lubrication | Lubricate the chain correctly-
54 | mechanical | chain drives | Broken pins. bushings, or rollers (continued) | Poorly fitted sprockets | Check the Sprockes for wear, and correct the bottom diameter.
54 | mechanical | chain drives | Broken pins. bushings, or rollers (continued) | Chain or sprocket corrosion | Remove any corrosion from the chain or sprocket, lubricate the chain correctly, and protect the chain and sprocke from further corrosion by keeping the chain clean and well lubricated.
55 | mechanical | chain drives | Pulsation | Chain tension too low | Adjust the take-ups to restore the proper tension.
55 | mechanical | chain drives | Pulsation | Chain speed too slow | Increase the size of the sprocket, or increase the conveyor Speed.
55 | mechanical | chain drives | Pulsation | Obstruction | Remove the obstruction, and ensure that the lower strand is not striking a foreign object.
55 | mechanical | chain drives | Pulsation | Heavy or tacky lubricants | Clean and lubricate the chain correctly.
55 | mechanical | chain drives | Pulsation | Sprockets with too few teeth, causing a large amount of chordal action | Replace with sprockets having the correct number of teeth.
55 | mechanical | chain drives | Pulsation | Eccentricity | Correct eccentricity ofhub hole.
56 | mechanical | chain drives | Broken sprocket teeth | Obstruction striking the cotter pins | Check the chain and sprocket clearances; Remove any foreign materials.
56 | mechanical | chain drives | Broken sprocket teeth | Excessive shock loads, especially with small, cast-iron sprockets | Reduce excessive shock loads, or change to steel Sprockets.
56 | mechanical | chain drives | Cotter pins coming out | Obstructions striking the cotter pins | Eliminate the obstruction; Tap the ends back until the cotter pin fits snugly against the side plates, or use a riveted chain.
56 | mechanical | chain drives | Cotter pins coming out | Cotter pins not installed properly, not spread apart and drawn back snugly against the side plates. | Correct the faulty installation.
57 | mechanical | chain drives | Damaged conveyed articles | Bent or damaged flights, attachments, or links | Repair or replace the damaged parts.
57 | mechanical | chain drives | Damaged conveyed articles | Obstruction in throughways or casings | Remove the obstruction.
57 | mechanical | chain drives | Damaged conveyed articles | Improper timing | Check timing sequence, chain elongation, and chain selection.
58 | mechanical | gear boxes | Noisy operation of the unit | Misalignment | Check the alignment of the unit; Check the condition of the coupling; If misalignment is the problem, have the maintenance group perform an alignment of the shafts.
58 | mechanical | gear boxes | Noisy operation of the unit | Faulty lubrication | Check oil level; Add lubricant if needed; Determine if lubricant is correct grade; If the lubricant is not the correct grade, replace with the correct lubricant.
58 | mechanical | gear boxes | Noisy operation of the unit | Excessive tension on the belts or the chain | Check the tension and the alignment of the drive auxiliaries, and relieve the tension if required
58 | mechanical | gear boxes | Noisy operation of the unit | Worn parts | Adjust or replace the worn parts.
58 | mechanical | gear boxes | Noisy operation of the unit | Overloading | Reduce the load.
59 | mechanical | gear boxes | Excessive operating temperature | Incorrect lubricant | Check the lubricant against the specification instructions; Replace with the correct lubricant.
59 | mechanical | gear boxes | Excessive operating temperature | Incorrect amount of lubricant | Check the level in the sight glass, and fill to the correct level; Ensure that the air breather is clean and functioning properly.
59 | mechanical | gear boxes | Excessive operating temperature | Overloading | Reduce the load.
59 | mechanical | gear boxes | Excessive operating temperature | Obstructed air flow | Check the air supply for proper fan circulation; Remove any obstructions; Avoid any high surrounding ambient temperatures; If the ambient temperature is high because of a local heat source, place some form of barrier between the heat source and the machine.
60 | mechanical | gear boxes | Oil leakage | Too much oil in the unit | Recheck the oil level with the unit shut down; Remove any excess oil.
60 | mechanical | gear boxes | Oil leakage | Clogged air breather | Remove the breather, and clean it.
60 | mechanical | gear boxes | Oil leakage | Loose bolts and nuts in jointed areas | Tighten all of the joints and end cap bolts.
60 | mechanical | gear boxes | Loosened mounting bolts | Vibration from fluctuating loads or misalignment | Check and realign the system; Tighten all of the bolts.
61 | mechanical | Lubricating Oil Systems | System pressure too low | Open drain-back valve from pressure line to return line | Close the pump relief valves.
61 | mechanical | Lubricating Oil Systems | System pressure too low | Pump relief valve or system pressure control valve set low | Check pump relief valves and the pressure control valve for normal Operation; Adjust as needed.
61 | mechanical | Lubricating Oil Systems | System pressure too low | Oil leak(s) in the system | Check for an oil leak; Repair as necessary.
61 | mechanical | Lubricating Oil Systems | System pressure too high | System pressure control valve set too high or not functioning properly | Check the system control valve, and adjust as needed.
61 | mechanical | Lubricating Oil Systems | System pressure too high | Plugged flow nozzle(s) | Check the flow controls for proper settings and positive indication of flow; Adjust the setting as necessary.
62 | mechanical | Lubricating Oil Systems | System pressure constantly fluctuating | System pressure control valve not functioning properly | Adjust the system pressure control valve to maintain a constant system pressure.
63 | mechanical | Lubricating Oil Systems | Very erratic pressures and sight flows, indicating a very uneven and burpy flow | Air being drawn into the system and pumped with the oil | Check the oil level in the reservoir and the free- floating operation of the floating suction; Verify there are no obstructions causing flowing suction to stick; Remove any debris from operation area; Check the suction line and the strainer to the pump for a possible air leak; Check the pressure tanks; If the tank is empty of oil, air may be leaking into the system from the air connection; Add oil as necessary.
63 | mechanical | Lubricating Oil Systems | Sounding of alarm | Dirty filter | Purge any air from the filter casing before changing over to the standby filter to put it into service.
63 | mechanical | Lubricating Oil Systems | Sounding of alarm | high differential pressure across the filter | Purge any air from the filter casing before changing over to the standby filter to put it into service.
64 | mechanical | Lubricating Oil Systems | Standby pump and alarm cycling on and off | Operating pump not running | Change the pump selector switch to reverse pumps; If the system now runs normally, investigate the pump taken out of service for a problem, such as a broken shaft.
64 | mechanical | Lubricating Oil Systems | Standby pump and alarm cycling on and off | Mercoid switches incorrectly set | Set the standby Mercoid switch approximately 5 and 15 psi below the desired system pressure.
64 | mechanical | Lubricating Oil Systems | Standby pump and alarm cycling on and off | Increased demand for oil from the system due to an oil leak | Look for oil leaks or some drastic change causing increased oil flow.
64 | mechanical | Lubricating Oil Systems | Standby pump and alarm cycling on and off | Oil temperature too high | Check that oil temperature on discharge side of cooler is within 10 °F of operational temperature; If it is not, make adjustments accordingly.
65 | mechanical | Lubricating Oil Systems | Pump running noisily | Low fluid level | Adjust the fluid supply to the pump.
65 | mechanical | Lubricating Oil Systems | Pump running noisily | System pressure too high | Adjust the pressure-relief valve to lower the pressure.
65 | mechanical | Lubricating Oil Systems | Pump running noisily | Variable-volume or pressure-compensated pump adjusted for too much flow | Adjust the pump.
65 | mechanical | Lubricating Oil Systems | Pump running noisily | Intake leaking | Locate and correct the leak
65 | mechanical | Lubricating Oil Systems | Pump running noisily | Pump speed too high | Decrease the pump speed.
65 | mechanical | Lubricating Oil Systems | Pump running noisily | Motor and pump not aligned | Have maintenance align the motor and pump.
65 | mechanical | Lubricating Oil Systems | Pump running noisily | Restricted intake | Find obstruction; clear intake; clean suction filters.
65 | mechanical | Lubricating Oil Systems | Pump running noisily | Worn pump | Repair or replace the pump.
66 | mechanical | Lubricating Oil Systems | Pump running noisily (continued) | Cavitation caused by lack of net positive suction head (NPSH) or turbulence from sharp pipe bends irmnediately upstream of the pump suction. | Lower the suction temperature.
66 | mechanical | Lubricating Oil Systems | Pump running noisily (continued) | suction pressure lower than the corresponding saturation temperature | Lower the suction temperature.
66 | mechanical | Lubricating Oil Systems | Pump running noisily (continued) | Recirculation of fluid at the impeller vane exit area | Avoid discharge restrictions. Increase the clearance at exit tips of vanes; /Never/ install higher horsepower driver without redesigning discharge and suction piping.
67 | mechanical | V-Belt Drives | Belt slipping | Not enough tension | Increase the tension. The deflection of the belt at midspan should be 1/64" for each inch of span between the centerlines of the driven and driving sheaves.
67 | mechanical | V-Belt Drives | Belt slipping | Drive overloaded | Increase the belt size.
67 | mechanical | V-Belt Drives | Belt slipping | Contaminants on belts or sheaves | Clean or change the belts or sheaves.
67 | mechanical | V-Belt Drives | Belt slipping | Heavy starting load | Increase the tension.
67 | mechanical | V-Belt Drives | Belt slipping | Not enough arc of contact | Lengthen the center distance, or use an idler.
68 | mechanical | V-Belt Drives | Belt turned over in sheave | Broken cords from prying belts on and off sheaves | Reduce the drive centers when you are installing the belts; Adjust the motor position to lessen the tension on the belts; Install new belts, and retention them.
68 | mechanical | V-Belt Drives | Belt turned over in sheave | Not enough tension | Increase the tension.
69 | mechanical | V-Belt Drives | Repeated belt breakage | Shock loads | Test the shaft runout for eccentricity; Have maintenance make repairs; Increase the tension or drive capacity.
69 | mechanical | V-Belt Drives | Repeated belt breakage | Broken cords from running or prying belts on and off sheaves | Reduce the drive centers when you are installing the belts; Adjust the motor position to lessen the tension on the belts; Install new belts, and retention them.
69 | mechanical | V-Belt Drives | Repeated belt breakage | Foreign objects falling into the sheaves | Provide protective guards.
70 | mechanical | V-Belt Drives | Rapid wear of the belt | Worn sheave grooves | Replace the sheaves.
70 | mechanical | V-Belt Drives | Rapid wear of the belt | Sheave diameter too small | Increase the sheave diameter.
70 | mechanical | V-Belt Drives | Rapid wear of the belt | Misalignment | Align the drive.
70 | mechanical | V-Belt Drives | Rapid wear of the belt | Drive overloaded | Increase the drive capacity.
70 | mechanical | V-Belt Drives | Rapid wear of the belt | Belts rubbing | Provide the correct running clearance.
70 | mechanical | V-Belt Drives | Rapid wear of the belt | Contaminated environment | Clean and protect the belts.
71 | mechanical | V-Belt Drives | Belt cracked and hardened, causing slippage | Excessive heat | Track down and eliminate the heat source; Provide ventilation.
71 | mechanical | V-Belt Drives | Belt whipping | Drive centers too long | Reduce the drive centers, or provide an idler.
71 | mechanical | V-Belt Drives | Belt whipping | Tensioner idler sheave out of adjustment | Reduce the drive centers, or provide an idler.
71 | mechanical | V-Belt Drives | Hot bearings | Inadequate bearing lubrication | lubricate the bearing.
71 | mechanical | V-Belt Drives | Hot bearings | Too much bearing lubricant | Open the vent/drain plug, and purge the lubricant cavity with fresh lubricant; Leave the vent open for approximately 30 minutes, and then close it
72 | mechanical | V-Belt Drives | Hot bearings (continued) | Drive belts too tight | Adjust the belt tension. The deflection of the belt at midspan should be 1/64" for each inch of span between the centerlines of the driven and driving sheaves.
73 | mechanical | V-Belt Drives | One or two belts broken in a set | Not a matched set of drive belts | Replace the drive belts with matching belts.
73 | mechanical | V-Belt Drives | One or two belts broken in a set | Belts broken internally because of poor installation practices | Move the motor inwards to detension the belts, and replace with matching belts, using the proper installation procedure; /Caution/ Do not use different manufacturers' belts to make up a set; Always use belts from one manufacturer because manufacturing processes differ from one manufacturer to another.
74 | mechanical | V-Belt Drives | Excessive belt stretch | Improper amount of take-up since the initial belt installation | Replace all the belts.
74 | mechanical | V-Belt Drives | Excessive belt stretch | Overload on the drive belt | Reduce the overload, or install a larger drive system.
74 | mechanical | V-Belt Drives | Excessive belt stretch | Internal breaks in the belt | Replace the belt; /Caution/ Never use a pry bar to install the belt in the sheave because this breaks the inner fibers on the belt and can break the sidewalls of the sheave.
75 | mechanical | V-Belt Drives | Unequal belt stretch | Not a matching set of belts | Replace With matching belts.
75 | mechanical | V-Belt Drives | Unequal belt stretch | Unequal coefficient of friction | Check and adjust the alignment of the sheaves, and correct the tension.
75 | mechanical | V-Belt Drives | Unequal belt stretch | Nonparallel shafts | Check and adjust the alignment of the sheaves, and correct the tension.
75 | mechanical | V-Belt Drives | Unequal belt stretch | Internal and nonvisible breaks in belts | Replace the belts.
75 | mechanical | V-Belt Drives | Unequal belt stretch | Broken belt cords | Replace the belts.
75 | mechanical | V-Belt Drives | Unequal belt stretch | Worn grooves in sheaves | Replaee the sheaves.
76 | mechanical | V-Belt Drives | Belt separation | Small sheaves | Replace with properly sized sheaves.
76 | mechanical | V-Belt Drives | Belt separation | Excessive belt tension | Check and adjust the belt tension.
76 | mechanical | V-Belt Drives | Topside belt wear | Belt obstruction | Remove the obstruction.
76 | mechanical | V-Belt Drives | Topside belt wear | Turned over or twisted belt | Adjust and inspect the belt. Replace as required.
76 | mechanical | V-Belt Drives | Opening of the envelope seam on belt | Rubber solvent or oil on the belt | Clean and inspect the belt. Replace the belt as required.
77 | mechanical | V-Belt Drives | Abnormal envelope wear | Abrasive condition, worn sheaves, improper sheave angle, slip, exposed to chemical fumes, obstructions, or high heat | Check the belt for an abrasive condition or any of the conditions mentioned as a probable cause; Replace the belts as required.
77 | mechanical | V-Belt Drives | Belt soft or swollen | Rubber solvent or oil on the belt | Clean and inspect the belt; Replace the belt as required.
77 | mechanical | V-Belt Drives | Belt envelope hardening and cracking | Exposure to severe heat and/or chemical fumes | Clean and inspect the belt; Replace the belt as required.
78 | mechanical | Fan Systems | Fan output below SCFM |  |  | ui
78 | mechanical | Fan Systems
78 | mechanical | Fan Systems
79 | mechanical | Fan Systems
79 | mechanical | Fan Systems
79 | mechanical | Fan Systems
79 | mechanical | Fan Systems
79 | mechanical | Fan Systems
80 | mechanical | Fan Systems
80 | mechanical | Fan Systems
81 | mechanical | Fan Systems
81 | mechanical | Fan Systems
81 | mechanical | Fan Systems
82 | mechanical | Fan Systems
82 | mechanical | Fan Systems
83 | mechanical | Fan Systems
83 | mechanical | Fan Systems
84 | mechanical | Fan Systems
85 | mechanical | Fan Systems
85 | mechanical | Fan Systems
85 | mechanical | Fan Systems
86 | mechanical | Fan Systems
86 | mechanical | Fan Systems
86 | mechanical | Fan Systems
87 | mechanical | Fan Systems
87 | mechanical | Fan Systems
88 | mechanical | Fan Systems
88 | mechanical | Fan Systems
89 | mechanical | Fan Systems